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Control, purpose and method
The Basis of Design (BoD) translates the client brief and Owner's Project Requirements (OPR) into measurable, coordinated design requirements. It records site conditions, option selection, assumptions, statutory approvals and the evidence needed for stage release. It does not replace calculations, specifications, the appointment, the BEP or actual permits.
1.  Lead consultant completes Part A: scope, jurisdiction, brief, site and code-adoption baseline.
2.  Competent discipline leads populate Part B: target/unit/comparison, verified source and clause, method, stage and owner. Independent checkers review the design and evidence.
3.  Authority coordinator screens every Part C row, adds site/use-specific submissions, confirms the current authority/service/checklist and planned review allowance.
4.  Lead consultant closes interfaces, options, assumptions and departures in Part D; LAP and task teams propagate one ChangeID to MIDP/TIDPs.
5.  Part E measures the exact stage/revision, checks actual authority conditions and records separate technical, client and statutory decisions before release.
The companion BBM-STD-12-APPROVALS-REGISTER-V0.1.xlsx (form; filename unchanged) contains every master approval and criterion, with separate criterion-stage evidence rows. This markdown is the office-template baseline; the populated project workbook is the single working tracker. Record the project BoD/workbook revisions together. After changing master B/C rows, regenerate/reconcile the workbook before release: the files do not synchronise automatically.
Decision (BIM Manager, 2026-10-14): Lead Design Consultant owns the integrated BoD; competent discipline leads own technical criteria; authority coordinator maintains external submissions; BIM Manager controls information records. Basis: appointment functions in ISO 19650-1/-2:2018 [R23] and office Directory/BEP (O-DEC-125). Actual role holders/delegation must be recorded in the project.
Decision (BIM Manager, 2026-10-14): No applicable mandatory criterion or approval prerequisite may be averaged away. Release requires current independent evidence and valid permissions/closed conditions for the exact next activity. Basis: office decision O-DEC-003; ISO 19650-4:2022 [R28] provides the exchange review context.
Document control and responsibilities
	Record
	Project entry and acceptance

	Project /​ client /​ site
	[ProjectID, client, plot, emirate, building/​zone and restricted distribution]

	Report /​ workbook
	[ContainerIDs, project Rnn revisions, template V0.2, issue date and CDE URIs]

	Appointment /​ responsibility
	[AppointmentIDs, scope, delegated design, exclusions, competent leads, deputy and reliance rights]

	Prepared /​ checked /​ approved /​ released
	[Distinct role-holder IDs, dates, signature/​decision evidence and exact revisions]

	Review trigger
	Every stage exchange and material brief, code, survey, occupancy, design, supplier, approval or programme change

	Revision /​ change /​ distribution
	[Previous/​current baseline, ChangeID, recipients, permitted use and acknowledgements]



Existing office authority and practice
•  Manual V0.5, BEP V0.5, OIR V0.3, Directory V0.3, Glossary V0.3 and office decisions V0.2 retain their existing authority. Codes and gate/status vocabularies are in the one code dictionary BBM-STD-93; UAE authority and submission detail is in BBM-STD-85.
•  Reuse O-DEC-001–007 and the single Clash Matrix V0.3 sections 2–3 O3-POL-01 naming/revision/suitability and evidence-based coordination rules. Default identity is CLIENT-ORG-PROJ-VOLUME-LEVEL-TYPE-ROLE-NUMBER.ext (O-DEC-102); Rnn is per-container revision metadata (O-DEC-113). One authorised appointment mapping takes precedence. Do not introduce another tolerance table.
•  SU-WIP / SU-COORD / SU-INFO / SU-REVIEW / SU-ISSUE express permitted use. Office CDE states WIP / Shared / Published / Archive are separate from workspace lifecycle folders, actual client acceptance and statutory approval.
•  MIDP V0.3 coordinates delivery commitments; TIDP V0.3 controls task-team production. Reuse their L1/L2/L3, correction, authorisation and client acceptance windows. Office planning allowances are not authority review timelines.
•  Guides BBM-STD-25 Guide V0.3 (initiation), BBM-STD-30 Guide V0.2 (coordinates), BBM-STD-32 Guide V0.2 (areas), BBM-STD-34 Guide V0.2 (stairs/ramps) and BBM-STD-36 Guide V0.2 (schedules) inform practical checks; they are training guides outside the controlled standard set. Correct model geometry, a schedule or a clash-free route does not alone prove code compliance.
Part A · Project definition
A1 · Client brief and project requirements
	Record
	Required project entry
	Evidence /​ owner

	Brief /​ OPR
	[Approved IDs/​revisions; purpose, functional outcomes, quality, cost/​programme limits]
	Client/​lead consultant reconcile conflicts

	OIR /​ PIR /​ AIR /​ EIR
	[Office/​client organisational decisions, project decisions, operational needs and appointment exchanges; RequirementIDs/​revisions]
	Office OIR is not client EIR. EIR means Exchange Information Requirements; OPR is separate

	Project type and occupancy
	[New/​existing/​alteration/​fit-out, use by floor, mixed-use, occupant population, hours and hazards]
	Architect, fire engineer and operator

	Design responsibilities
	[Buildings/​zones, disciplines, specialist/​delegated design, scope exclusions and interface owners]
	Appointment and detailed responsibility matrix

	Cost, procurement and options
	[Capex/​opex basis/​date, contingency, whole-life boundary, procurement and package strategy]
	Client and cost consultant

	Phasing and occupation
	[Phase boundaries, temporary services/​routes, separable permits and partial occupation]
	Lead/​fire/​contractor plus actual authority consent

	Stages and milestones
	[RIBA stage by package, ExchangeID, DeliveryID, decision/​issue dates]
	Approved programme and MIDP; stage is not a permit

	Operation and acceptance
	[FM representative, working life, maintenance, AIR, commissioning and POE plan]
	Client/​asset owner and competent leads



RIBA Plan of Work 2020 [R25]: 0 Strategic Definition; 1 Preparation and Briefing; 2 Concept Design; 3 Spatial Coordination; 4 Technical Design; 5 Manufacturing and Construction; 6 Handover; 7 Use. Stages 4/5 can overlap by package. Keep actual authority and procurement dependencies separate from this stage context.
A2 · Site data and measurement conventions
	Input
	Project value /​ units
	Controlled source and check

	Plot /​ affection plan
	[PlotID, land area m2, boundaries, title/​lease/​easements]
	Authenticated current plot/​affection plan and survey

	Planning envelope
	[Use, FAR, GFA/​BUA limits, coverage %, setbacks m, height/​datum m, storeys]
	Written planning/​master-developer conditions and exceptions

	Area basis
	[Authority GFA; client BUA, net/​usable definitions; exclusions/​voids]
	Signed measurement rule; reconcile each floor with model/​schedules

	Parking/​loading
	[Ratios by use; total/​accessible/​EV/​cycle/​loading counts and geometry]
	Actual adopted ratios and traffic/​access approval

	Coordinates/​terrain
	[CRS with EPSG code and transformation, horizontal/​vertical datum, units, benchmark and uncertainty. Dubai default: DLTM, EPSG:3997 "WGS 84 /​ Dubai Local TM", vertical datum DMD (Dubai Municipality Datum = Port Rashid datum, no EPSG code). Abu Dhabi: the CRS stated in the ADM/​DMT survey and CAD/​BIM submission guideline for the plot; vertical datum Ras Ghumays (EPSG datum 1146)]
	Surveyor evidence, ≥3 well-distributed control points plus elevation/​unit probes (O-DEC-106) and independent alignment/​export test; register in BBM-STD-86 and BEP §8.2

	Ground/​groundwater
	[Report revision, investigation coverage, bearing/​settlement and groundwater m datum]
	Geotechnical interpretation and structural adoption

	Climate/​exposure/​flood
	[Station/​year, statistical weather basis, wind/​seismic basis, flood event/​datum, corrosion]
	Controlled datasets and adopted design/​authority source

	Utilities/​protected assets
	[Capacity, connection points/​inverts, easements, asset locations and verification confidence]
	Operator records/​NOCs and justified field verification

	Environment/​heritage/​neighbours
	[Ecology, contamination, heritage, noise receptors and adjoining structures]
	Screening, baseline surveys and consent conditions



A3 · Code adoption and jurisdiction
Decision (BIM Manager, 2026-10-14): Freeze project code applicability, exact editions/amendments, transition dates, jurisdiction and verified clauses before technical reliance. The newest publication is not automatically the adopted code. Basis: official AD/Dubai publications [R02, R03, R17, R18] (O-DEC-126).
Code adoption is recorded once, in the edition and adoption register of BBM-STD-51 §3 (O-DEC-111): instrument ID, instrument, edition, date, URL and source-check date. The project applicability and clause record for each instrument is kept in the BBM-STD-57 Codes table under the same ID. Each Part B criterion cites that register ID (ED-…, e.g. ED-DBC, ED-ADIBC, ED-UAE-FLS) in its source cell, and the References table below gives the ED-ID for every BoD reference; this BoD keeps no separate code list. UAE requirement detail (Dubai BIM permit profile, DBC, Law 3/2026 and its circular 11-9-1, fire code, Abu Dhabi codes, green-building minimums) is owned by BBM-STD-85. The former AdoptionID CODE-nnn is retired; any issued CODE-nnn maps once to its register ID.
Obtain the applicable discipline volumes and referenced-standard editions, including structural loads/materials and MEP standards. No clause number is inferred from a catalogue abstract. Accessibility sources are split by emirate: Abu Dhabi uses R04; Dubai uses the accessibility provisions of the DBC [R17] and any Dubai accessibility code named by the competent authority [R41], edition checked at project start and recorded in the BBM-STD-51 §3 register. If requirements conflict, record both and obtain competent contractual/statutory/design resolution under the appointment hierarchy; do not cherry-pick a value. Client targets may exceed legal minima but cannot waive law; split them into linked criteria where checks differ.
Part B · Measurable design criteria
B0 · How to populate and verify
Each master criterion below requires project target, units/category, comparison (minimum/maximum/range/exact/category), scope/location, verified code adoption/clause, actual result, uncertainty/tolerance where relevant, checker and exact evidence revision. Split different uses/zones into separately identified rows. No universal engineering number, climatic condition, parking ratio, travel limit or clearance is imposed here.
RIBA 0–7 are RIBA Plan of Work 2020 stages (not issue severities S1–S3). Reconfirm every listed stage: RIBA 2/3 coordinated predictions/calculations; RIBA 4 frozen technical design/specifications; RIBA 5 approved products/installations/inspection; RIBA 6 witnessed commissioning/as-built/acceptance; RIBA 7 measured use and agreed performance review. RIBA 1 information criteria define the requirements baseline. A design prediction cannot pass an installation test. N/A requires a separate approved basis for each criterion-stage.
B1 · Architecture
	CriterionID
	Criterion
	Requirement
	Project value /​ unit
	Source code & clause
	Verification method
	Stages
	Owner

	AR-01
	Land use and occupancy
	Confirm permitted use and population by floor
	[use class; persons/​floor]
	R02 ADIBC edition in force at project start and R04 accessibility (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Reconcile plot controls, brief and occupancy schedule
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead

	AR-02
	Plot and setbacks
	Keep structures/​projections within approved envelope
	[plot m2; setbacks m]
	R02 ADIBC edition in force at project start and R04 accessibility (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Overlay authenticated affection plan and dimensioned survey/​site plan
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead

	AR-03
	Height and storeys
	Meet datum-specific height and storey limits including roof plant
	[m datum; storeys]
	R02 ADIBC edition in force at project start and R04 accessibility (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Survey-based coordinated sections and aviation constraints
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead

	AR-04
	FAR and regulated GFA
	Apply authority area inclusions/​exclusions and maximum FAR
	[FAR ratio; GFA m2]
	R02 ADIBC edition in force at project start and R04 accessibility (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Reconcile regulated areas floor by floor with signed convention
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead

	AR-05
	BUA and client areas
	Keep BUA, usable/​net areas separate from regulated GFA
	[BUA/​NIA m2; efficiency %]
	R02 ADIBC edition in force at project start and R04 accessibility (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Reconcile brief and room/​area schedules with all exclusions
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead

	AR-06
	Space standards
	Meet room areas, widths, adjacencies and space-per-person basis
	[m2/​space; m; persons]
	R02 ADIBC edition in force at project start and R04 accessibility (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Room schedule and functional adjacency review
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead

	AR-07
	Clear heights
	Meet finished clear heights and headroom including obstructions
	[m per space/​route]
	R02 ADIBC edition in force at project start and R04 accessibility (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Dimensioned coordinated sections including finishes/​services
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead

	AR-08
	Parking and loading
	Meet approved parking, accessible/​EV/​cycle/​loading provision
	[ratio; spaces; bay m]
	R02 ADIBC edition in force at project start and R04 accessibility (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Demand, geometry, swept paths and traffic approval reconciliation
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead

	AR-09
	Accessible arrival and circulation
	Provide continuous accessible routes, entrances, doors and transitions
	[width m; slope/​crossfall %; rise mm]
	R02 ADIBC and R04 accessibility (AD); R17 /​ ED-DBC DBC accessibility provisions and R41 (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Whole-route dimensioned audit; model limits alone do not prove compliance
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead

	AR-10
	Accessible facilities and wayfinding
	Meet toilet, refuge, tactile, signage and assistance requirements
	[facilities; clearance/​reach mm]
	R02 ADIBC and R04 accessibility (AD); R17 /​ ED-DBC DBC accessibility provisions and R41 (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	User-journey and competent accessibility review
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead

	AR-11
	Facade and glazing
	Meet heat/​solar, air/​water leakage, safety and maintenance requirements
	[U W/​m2K; SHGC; WWR %; leakage unit]
	R02 ADIBC edition in force at project start and R04 accessibility (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Envelope calculations, certified system details and test plan
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead

	AR-12
	Acoustics
	Meet room/​external noise, separation and reverberation targets
	[dB metric; seconds]
	R02 ADIBC edition in force at project start and R04 accessibility (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Acoustic calculation and specified field tests/​conditions
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead

	AR-13
	Daylight and glare
	Meet selected daylight/​glare method for occupied spaces
	[lux/​metric; hours; glare index]
	R02 ADIBC edition in force at project start and R04 accessibility (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Simulation with frozen climate, use, glazing and shading inputs
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead

	AR-14
	Vertical transport planning
	Meet capacity, waiting/​service and accessibility/​fire requirements
	[persons; interval s; kg; m/​s]
	R02 ADIBC edition in force at project start and R04 accessibility (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Lift traffic analysis and fire/​architecture interface review
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead

	AR-15
	Servicing and fire access
	Provide safe loading, fire-vehicle access and equipment replacement routes
	[clear/​turning m; kN]
	R02 ADIBC edition in force at project start and R04 accessibility (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Swept paths and replacement sequence with structural/​MEP/​fire review
	RIBA 2;3;4;5;6;7
	Architect /​ planning lead



B2 · Fire and life safety
	CriterionID
	Criterion
	Requirement
	Project value /​ unit
	Source code & clause
	Verification method
	Stages
	Owner

	FL-01
	Fire strategy and classification
	Classify uses, hazards, mixed occupancy and height category
	[use/​hazard class; persons; height m]
	R03 UAE FLS Code 2018; R30 local Civil Defence; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Signed fire strategy reconciled to approved occupancy/​plans
	RIBA 2;3;4;5;6;7
	Fire engineer /​ Civil Defence liaison

	FL-02
	Occupant load
	Calculate floor occupants using adopted factors and actual use
	[persons; m2/​person]
	R03 UAE FLS Code 2018; R30 local Civil Defence; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Checked floor-area/​factor/​operational capacity reconciliation
	RIBA 2;3;4;5;6;7
	Fire engineer /​ Civil Defence liaison

	FL-03
	Exit number and capacity
	Meet exit number, width, remoteness, independence and discharge
	[count; clear mm; persons]
	R03 UAE FLS Code 2018; R30 local Civil Defence; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Egress calculations including shared stairs and final discharge
	RIBA 2;3;4;5;6;7
	Fire engineer /​ Civil Defence liaison

	FL-04
	Travel distance and dead ends
	Meet actual travel/​common-path/​dead-end limits for adopted conditions
	[m per condition]
	R03 UAE FLS Code 2018; R30 local Civil Defence; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Measure paths around obstacles with sprinkler/​use assumptions explicit
	RIBA 2;3;4;5;6;7
	Fire engineer /​ Civil Defence liaison

	FL-05
	Compartmentation
	Meet compartment size, separation and opening/​shaft protection
	[m2; fire rating minutes]
	R03 UAE FLS Code 2018; R30 local Civil Defence; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Fire plans plus rated walls/​doors/​penetration interface schedules
	RIBA 2;3;4;5;6;7
	Fire engineer /​ Civil Defence liaison

	FL-06
	Structural fire resistance
	Meet member/​assembly fire performance for actual use/​height
	[minutes; assembly IDs]
	R03 UAE FLS Code 2018; R30 local Civil Defence; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Fire/​structural design and approved protection specification
	RIBA 2;3;4;5;6;7
	Fire engineer /​ Civil Defence liaison

	FL-07
	Facade fire performance
	Demonstrate whole-system performance and cavity/​perimeter barriers
	[test standard/​class; barrier m]
	R03 UAE FLS Code 2018; R30 local Civil Defence; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Civil Defence facade submission and full tested-system scope
	RIBA 2;3;4;5;6;7
	Fire engineer /​ Civil Defence liaison

	FL-08
	Smoke management
	Meet smoke zoning, exhaust/​make-up, pressure and tenability basis
	[m3/​s; Pa; time/​tenability]
	R03 UAE FLS Code 2018; R30 local Civil Defence; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Smoke calculation/​modelling, controls matrix and integrated test script
	RIBA 2;3;4;5;6;7
	Fire engineer /​ Civil Defence liaison

	FL-09
	Firefighting water and suppression
	Meet hazard-specific coverage, storage, flow, pressure and duration
	[L/​min; bar; m3; min]
	R03 UAE FLS Code 2018; R30 local Civil Defence; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Hydraulic calculations, pumps/​tanks/​sprinkler/​hydrant approval
	RIBA 2;3;4;5;6;7
	Fire engineer /​ Civil Defence liaison

	FL-10
	Detection and alarm
	Meet detection, zoning, audibility/​visibility and interfaces
	[zones/​devices; dB; matrix ID]
	R03 UAE FLS Code 2018; R30 local Civil Defence; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Approved layout/​cause-effect and witnessed fail-state tests
	RIBA 2;3;4;5;6;7
	Fire engineer /​ Civil Defence liaison

	FL-11
	Emergency lighting and power
	Maintain escape illumination and life-safety continuity
	[lux; min; kVA/​UPS]
	R03 UAE FLS Code 2018; R30 local Civil Defence; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Point calculations, load/​autonomy tests and power-failure scenario
	RIBA 2;3;4;5;6;7
	Fire engineer /​ Civil Defence liaison

	FL-12
	Fire appliance facilities
	Provide unobstructed access, hardstanding and required facilities
	[width/​turning m; kN; count]
	R03 UAE FLS Code 2018; R30 local Civil Defence; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Swept-path/​site review and Civil Defence inspection
	RIBA 2;3;4;5;6;7
	Fire engineer /​ Civil Defence liaison

	FL-13
	Evacuation and operation
	Address refuge, assisted evacuation, phased use and procedures
	[refuge persons; scenario IDs]
	R03 UAE FLS Code 2018; R30 local Civil Defence; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Fire engineer/​operator review and handover/​drill acceptance
	RIBA 2;3;4;5;6;7
	Fire engineer /​ Civil Defence liaison



[image: BBM_LOGO]
[image: BBM_LOGO]BBM-BIM | BBM-STD-12-BASIS_OF_DESIGN_REPORT-V0.3



2 | Page

B3 · Structure
	CriterionID
	Criterion
	Requirement
	Project value /​ unit
	Source code & clause
	Verification method
	Stages
	Owner

	ST-01
	Code and structural system
	Freeze codes, amendments, analysis and robustness basis
	[code edition; system; consequence class]
	R02 ADIBC edition in force at project start and adopted references (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Signed design-code schedule and independent analysis review
	RIBA 2;3;4;5;6;7
	Structural engineer

	ST-02
	Geotechnical basis
	Adopt verified ground, groundwater, bearing and settlement basis
	[kPa; mm; groundwater m datum]
	R02 ADIBC edition in force at project start and adopted references (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Geotechnical factual/​interpretive reports and designer adoption
	RIBA 2;3;4;5;6;7
	Structural engineer

	ST-03
	Permanent and imposed loads
	Schedule use-specific dead/​live/​partition/​plant/​construction actions
	[kPa; kN]
	R02 ADIBC edition in force at project start and adopted references (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Trace load take-off to occupancy, facade, roof and equipment data
	RIBA 2;3;4;5;6;7
	Structural engineer

	ST-04
	Wind actions
	Verify wind speed, exposure, return period and dynamic method
	[m/​s; years; exposure; kPa]
	R02 ADIBC edition in force at project start and adopted references (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Adopted hazard data and calculations; wind tunnel where required
	RIBA 2;3;4;5;6;7
	Structural engineer

	ST-05
	Seismic actions
	Verify hazard, site class, importance, ductility and response basis
	[hazard parameters; class; factors]
	R02 ADIBC edition in force at project start and adopted references (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Adopted spectrum plus geotechnical/​structural review
	RIBA 2;3;4;5;6;7
	Structural engineer

	ST-06
	Combinations and stability
	Check combinations, load path, uplift, overturning and accidental cases
	[combination IDs; utilisation]
	R02 ADIBC edition in force at project start and adopted references (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Independent model/​input/​units and calculation review
	RIBA 2;3;4;5;6;7
	Structural engineer

	ST-07
	Materials and strengths
	Specify concrete, rebar, steel/​connection grades for exposure/​use
	[MPa; grades; standard editions]
	R02 ADIBC edition in force at project start and adopted references (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Design/​material schedules, specifications and certification/​test plan
	RIBA 2;3;4;5;6;7
	Structural engineer

	ST-08
	Durability and design life
	Meet working life, cover, corrosion, exposure and crack requirements
	[years; cover/​crack mm; exposure]
	R02 ADIBC edition in force at project start and adopted references (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Durability strategy tied to site evidence and maintenance
	RIBA 2;3;4;5;6;7
	Structural engineer

	ST-09
	Serviceability and movement
	Control deflection, drift, vibration and differential movement
	[mm; ratios; Hz; acceleration]
	R02 ADIBC edition in force at project start and adopted references (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Analysis with facade/​partition/​MEP movement interfaces
	RIBA 2;3;4;5;6;7
	Structural engineer

	ST-10
	Temporary works and foundations
	Demonstrate excavation, shoring, dewatering and adjacent-asset safety
	[depth m; movement mm; triggers]
	R02 ADIBC edition in force at project start and adopted references (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Approved sequence/​design, monitoring and relevant permits
	RIBA 2;3;4;5;6;7
	Structural engineer

	ST-11
	Openings and plant supports
	Verify openings, fixings, plant reactions and replacement loads
	[mm; kN; dynamic factor]
	R02 ADIBC edition in force at project start and adopted references (AD); R17 /​ ED-DBC DBC as amended (Dubai); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Opening/​support register and signed design before cutting
	RIBA 2;3;4;5;6;7
	Structural engineer



B4 · MEP and vertical transport
	CriterionID
	Criterion
	Requirement
	Project value /​ unit
	Source code & clause
	Verification method
	Stages
	Owner

	ME-01
	Outdoor HVAC conditions
	Adopt station, statistical basis, dry/​wet bulb and extreme conditions
	[degC DB/​WB; occurrence %; station/​year]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Controlled climatic data and mechanical designer approval
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-02
	Indoor HVAC conditions
	Set occupied/​unoccupied temperature, humidity and tolerance per space
	[degC; RH %; tolerance]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Room data sheets and client/​operator comfort review
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-03
	Cooling/​heating load and diversity
	Size from documented envelope, occupancy, equipment and diversity
	[kW; W/​m2; ratio]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Checked load model and reconciled architecture/​process inputs
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-04
	Ventilation and IAQ
	Meet occupancy ventilation, filtration and contaminant criteria
	[L/​s/​person; L/​s/​m2; filter class]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Room-by-room calculation and balancing/​IAQ test plan
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-05
	Exhaust and pressures
	Meet kitchen/​toilet/​car park/​specialist exhaust and pressure relationships
	[L/​s; ACH; Pa]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; R03 UAE FLS Code 2018 (fire interface); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Air balance and fire/​smoke interface with operating tests
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-06
	Plant efficiency and redundancy
	Meet agreed part-load efficiency and resilience requirements
	[COP/​seasonal metric; N or N+1; kW]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Selections, certificates and failure-mode assessment
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-07
	Ducts and pipes
	Meet pressure/​velocity/​insulation/​acoustic requirements
	[Pa/​m; m/​s; thickness mm; dB]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Sizing calculations and coordinated insulated sections
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-08
	Potable water demand and storage
	Meet demand, storage, pressure, quality and backflow basis
	[L/​person/​day; m3; bar; quality limits]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Demand/​storage calculation, utility approval and flushing/​sampling
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-09
	Hot water safety and recovery
	Meet demand, recovery, hygiene and scalding protection
	[L/​day; kW; degC; min]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Demand/​distribution analysis and health-risk commissioning
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-10
	Drainage, sewer and vents
	Meet discharge, pipe sizing, venting, connection levels/​capacity
	[L/​s; mm; gradient %; invert m]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Drainage calculations, riser review and sewer operator approval
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-11
	Stormwater and attenuation
	Meet adopted event, runoff, discharge cap and storage
	[years; mm/​h; L/​s; m3]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Hydrology/​hydraulics with climate allowance and overflow routes
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-12
	Fire-system interfaces
	Align fire MEP/​power/​controls with signed strategy
	[hydraulic/​electrical/​matrix IDs]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; R03 UAE FLS Code 2018 (fire interface); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Trace requirements and test fail states across disciplines
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-13
	Electricity demand and supply
	Reconcile connected/​diversified loads, voltage and network offer
	[kW; kVA; V; diversity; PF]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Load schedule, SLD and utility capacity/​connection approval
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-14
	Protection and earthing
	Meet fault, discrimination, earthing, lightning and touch-voltage basis
	[kA; ohm; ms; protection class]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Checked studies, device settings and test certificates
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-15
	Emergency and standby power
	Meet autonomy and transfer/​fail-safe requirements for critical loads
	[kVA; minutes/​hours; transfer s]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; R03 UAE FLS Code 2018 (fire interface); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Essential-load list, autonomy study and blackout test
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-16
	Lighting and controls
	Meet maintained illuminance, glare, colour and energy criteria
	[lux; glare metric; W/​m2; zones]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Photometric study with reflectance/​maintenance factors and measurements
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-17
	ELV, ICT and telecom
	Meet capacity, coverage, rooms, containment and operator requirements
	[ports; bandwidth; room m2; coverage %]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Operator-approved schematics and cabling/​coverage tests
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-18
	BMS and metering
	Meet points, control sequence, alarms, trends and metering requirements
	[points; intervals; meter accuracy]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Points/​sequence matrix and witnessed controls/​data-export tests
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-19
	Lift/​escalator engineering
	Coordinate pits/​headroom, loads, power, ventilation, rescue and certification
	[mm; kN; kW; kg]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Supplier data across structure/​MEP/​fire and statutory tests
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-20
	Gas and specialist systems
	Meet licensed gas/​fuel/​medical/​process scope and adopted rules
	[bar; flow; storage; separation m]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Specialist design, risk assessment and authority inspection
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist

	ME-21
	Maintainability and commissioning
	Provide safe isolation, access, removal and testing
	[clear mm; loads; test count]
	R02 ADIBC (AD) or R17 /​ ED-DBC DBC as amended (Dubai); R08/​R09 TAQA where Abu Dhabi; R19 DEWA where Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Replacement-route demonstration and operator maintenance review
	RIBA 2;3;4;5;6;7
	MEP leads /​ lift specialist



B5 · Sustainability
	CriterionID
	Criterion
	Requirement
	Project value /​ unit
	Source code & clause
	Verification method
	Stages
	Owner

	SU-01
	Scheme and rating
	Select jurisdiction, scheme/​version/​bulletins and contractual rating. Statutory minimum: Abu Dhabi 1 Pearl (private) /​ 2 Pearl (government-funded) per DMT 8 January 2025 [R07]; Dubai Al Sa'fat Silver Sa'fa for all new buildings [R18]. Client targets may exceed, never undercut, the minimum
	[PBRS/​PVRS/​PCRS/​Al Sa'fat; rating]
	R05 PBRS v1.0 April 2010; R06 bulletin 3 2011; R07 2025; R18 Al Sa'fat January 2023; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Authority/​client applicability decision; never mix scheme credit thresholds
	RIBA 2;3;4;5;6;7
	Sustainability lead /​ PQP

	SU-02
	Required credits
	Track every applicable mandatory credit and stage evidence
	[credit IDs; complete/​applicable]
	R05 PBRS v1.0 April 2010; R06 bulletin 3 2011; R07 2025; R18 Al Sa'fat January 2023; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	PQP matrix with owners and actual authority decisions
	RIBA 2;3;4;5;6;7
	Sustainability lead /​ PQP

	SU-03
	Energy target
	Meet adopted baseline comparison and absolute operating energy target
	[kWh/​m2/​year; reduction %]
	R05 PBRS v1.0 April 2010; R06 bulletin 3 2011; R07 2025; R18 Al Sa'fat January 2023; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Checked energy model, weather, schedules and regulated/​unregulated boundaries
	RIBA 2;3;4;5;6;7
	Sustainability lead /​ PQP

	SU-04
	Water target
	Meet indoor/​outdoor demand and reuse/​metering criteria
	[L/​person/​day; m3/​year; reduction %]
	R05 PBRS v1.0 April 2010; R06 bulletin 3 2011; R07 2025; R18 Al Sa'fat January 2023; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Fixtures/​irrigation water balance and source quality/​availability
	RIBA 2;3;4;5;6;7
	Sustainability lead /​ PQP

	SU-05
	Passive/​envelope performance
	Meet thermal, shading, orientation and air-leakage criteria
	[U W/​m2K; SHGC; test leakage unit]
	R05 PBRS v1.0 April 2010; R06 bulletin 3 2011; R07 2025; R18 Al Sa'fat January 2023; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Energy/​envelope reconciliation and testing strategy
	RIBA 2;3;4;5;6;7
	Sustainability lead /​ PQP

	SU-06
	Materials and waste
	Meet sourcing, embodied-impact and diversion requirements
	[kgCO2e/​m2; % by mass; credit IDs]
	R05 PBRS v1.0 April 2010; R06 bulletin 3 2011; R07 2025; R18 Al Sa'fat January 2023; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	EPDs/​system boundary, procurement and waste evidence
	RIBA 2;3;4;5;6;7
	Sustainability lead /​ PQP

	SU-07
	Ecology and outdoor comfort
	Meet habitat, heat-island, shade and external comfort criteria
	[habitat m2; shade % at set time; metric]
	R05 PBRS v1.0 April 2010; R06 bulletin 3 2011; R07 2025; R18 Al Sa'fat January 2023; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Ecology and microclimate studies coordinated to landscape
	RIBA 2;3;4;5;6;7
	Sustainability lead /​ PQP

	SU-08
	Construction and operating verification
	Meet construction rating, commissioning and measured-use obligations
	[rating decision; tests; reporting period]
	R05 PBRS v1.0 April 2010; R06 bulletin 3 2011; R07 2025; R18 Al Sa'fat January 2023; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Credit closeout, commissioning, FM training and post-occupancy review
	RIBA 2;3;4;5;6;7
	Sustainability lead /​ PQP




B6 · Civil infrastructure and utilities
	CriterionID
	Criterion
	Requirement
	Project value /​ unit
	Source code & clause
	Verification method
	Stages
	Owner

	CI-01
	Survey and coordinates
	Use verified plot, CRS, datum, benchmark, units and accuracy
	[CRS: Dubai DLTM EPSG:3997 with vertical datum DMD unless the authority states otherwise; Abu Dhabi: the CRS in the ADM/​DMT survey and CAD/​BIM submission guideline, EPSG code + transformation, vertical datum Ras Ghumays; m; uncertainty mm; CRS record ID per BBM-STD-86 §6]
	R01 DMT 2025; R08 TAQA 2024; R09 sewer; R10 traffic; R19/​R20 Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Survey control and independent model/​site alignment
	RIBA 2;3;4;5;6;7
	Civil /​ infrastructure lead

	CI-02
	Utilities and easements
	Locate protected assets and applicable clearances/​easements
	[routes/​depth m; easement m; confidence]
	R01 DMT 2025; R08 TAQA 2024; R09 sewer; R10 traffic; R19/​R20 Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Operator records and justified field verification/​NOCs
	RIBA 2;3;4;5;6;7
	Civil /​ infrastructure lead

	CI-03
	Water connection
	Confirm capacity, point, pressure, metering and fire-water basis
	[L/​s; bar; mm]
	R01 DMT 2025; R08 TAQA 2024; R09 sewer; R10 traffic; R19/​R20 Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Operator written conditions and hydraulic calculations
	RIBA 2;3;4;5;6;7
	Civil /​ infrastructure lead

	CI-04
	Sewer and recycled water
	Confirm discharge quality/​capacity, inverts and reuse supply
	[L/​s; invert m; quality]
	R01 DMT 2025; R08 TAQA 2024; R09 sewer; R10 traffic; R19/​R20 Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Operator approval and network analysis; distinguish private disposal
	RIBA 2;3;4;5;6;7
	Civil /​ infrastructure lead

	CI-05
	Power and telecom corridors
	Reserve substations, ducts, rooms and protected routes
	[kVA; counts; corridor m]
	R01 DMT 2025; R08 TAQA 2024; R09 sewer; R10 traffic; R19/​R20 Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Composite utility design and operator approvals
	RIBA 2;3;4;5;6;7
	Civil /​ infrastructure lead

	CI-06
	Flood and surface drainage
	Protect buildings/​neighbours for agreed flood scenarios
	[flood datum/​freeboard m; years]
	R01 DMT 2025; R08 TAQA 2024; R09 sewer; R10 traffic; R19/​R20 Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Catchment model, exceedance paths and authority acceptance
	RIBA 2;3;4;5;6;7
	Civil /​ infrastructure lead

	CI-07
	Roads, access and traffic
	Meet approved demand, visibility, swept paths and pedestrian safety
	[trips/​hour; visibility m; capacity ratio]
	R01 DMT 2025; R08 TAQA 2024; R09 sewer; R10 traffic; R19/​R20 Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Agreed TIS, road/​access design and inspection
	RIBA 2;3;4;5;6;7
	Civil /​ infrastructure lead

	CI-08
	Earthworks and retaining interfaces
	Control grading, cut/​fill, erosion and adjacent movement
	[m3; slope; levels m; movement mm]
	R01 DMT 2025; R08 TAQA 2024; R09 sewer; R10 traffic; R19/​R20 Dubai; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Earthworks balance, geotechnical/​structural design and monitoring
	RIBA 2;3;4;5;6;7
	Civil /​ infrastructure lead



B7 · Landscape and site
	CriterionID
	Criterion
	Requirement
	Project value /​ unit
	Source code & clause
	Verification method
	Stages
	Owner

	LA-01
	Planting and biodiversity
	Meet species, habitat, soil and mature canopy/​root requirements
	[native %; soil m3; habitat m2; species]
	R05 PBRS 2010; R11 EAD 2022; R04 accessibility (AD); R18 Al Sa'fat 2023; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Plant/​soil schedule, ecology and structure/​utility review
	RIBA 2;3;4;5;6;7
	Landscape architect

	LA-02
	Irrigation and reuse
	Meet seasonal water budget and approved source quality
	[m3/​day; L/​m2/​day; season factors]
	R05 PBRS 2010; R11 EAD 2022; R04 accessibility (AD); R18 Al Sa'fat 2023; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Irrigation balance/​zoning and written supply consent
	RIBA 2;3;4;5;6;7
	Landscape architect

	LA-03
	Accessible external routes
	Meet route width/​slope, surface, shade and wayfinding criteria
	[m; slope %; surface class; shade %]
	R05 PBRS 2010; R11 EAD 2022; R04 accessibility (AD); R17 /​ ED-DBC DBC accessibility provisions and R41 (Dubai); R18 Al Sa'fat 2023; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Continuous arrival/​destination audit and materials review
	RIBA 2;3;4;5;6;7
	Landscape architect

	LA-04
	External lighting and furniture
	Meet safety, glare/​spill, durability and accessible placement
	[lux; spill metric; clear mm; class]
	R05 PBRS 2010; R11 EAD 2022; R04 accessibility (AD); R18 Al Sa'fat 2023; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Photometric/​site plan and night/​operator inspection
	RIBA 2;3;4;5;6;7
	Landscape architect

	LA-05
	Levels and landscape loads
	Coordinate thresholds, drainage, waterproofing and saturated loads
	[levels m; falls %; saturated kPa]
	R05 PBRS 2010; R11 EAD 2022; R04 accessibility (AD); R18 Al Sa'fat 2023; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Roof/​site sections, structural loads and drainage review
	RIBA 2;3;4;5;6;7
	Landscape architect




B8 · Security
	CriterionID
	Criterion
	Requirement
	Project value /​ unit
	Source code & clause
	Verification method
	Stages
	Owner

	SE-01
	Threat and risk basis
	Set proportionate protected zones and response scenarios
	[risk categories; zones; response minutes]
	R26 ISO 19650-5:2020 (information security only; triage per BBM-STD-87); Dubai: security-system drawings follow the current SIRA/​DM requirement for the plot, confirmed at permit stage; Abu Dhabi: competent security authority confirmed at permit stage; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Client/​operator risk assessment and statutory screening
	RIBA 2;3;4;5;6;7
	Security specialist /​ operator

	SE-02
	Physical security and escape
	Meet access/​perimeter protection while maintaining emergency release
	[door/​zone classes; clearance m]
	R26 ISO 19650-5:2020 (information security only; triage per BBM-STD-87); Dubai: security-system drawings follow the current SIRA/​DM requirement for the plot, confirmed at permit stage; Abu Dhabi: competent security authority confirmed at permit stage; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Security/​fire/​accessibility joint review and fail-safe tests
	RIBA 2;3;4;5;6;7
	Security specialist /​ operator

	SE-03
	CCTV and access systems
	Meet authorised coverage, image quality, retention and privacy
	[coverage %; pixel metric; days; uptime]
	R26 ISO 19650-5:2020 (information security only; triage per BBM-STD-87); Dubai: security-system drawings follow the current SIRA/​DM requirement for the plot, confirmed at permit stage; Abu Dhabi: competent security authority confirmed at permit stage; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Actual security regulator/​operator design approval and witnessed tests
	RIBA 2;3;4;5;6;7
	Security specialist /​ operator

	SE-04
	Information and cyber security
	Protect sensitive designs, access rights and network interfaces
	[roles; retention; recovery objectives]
	R26 ISO 19650-5:2020 (information security only; triage per BBM-STD-87); Dubai: security-system drawings follow the current SIRA/​DM requirement for the plot, confirmed at permit stage; Abu Dhabi: competent security authority confirmed at permit stage; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Sensitivity, segregation/​access and recovery tests; controlled handover
	RIBA 2;3;4;5;6;7
	Security specialist /​ operator



B9 · BIM and information
	CriterionID
	Criterion
	Requirement
	Project value /​ unit
	Source code & clause
	Verification method
	Stages
	Owner

	IM-01
	Requirement traceability
	Trace criteria to OPR/​brief, PIR/​AIR and appointment EIR
	[RequirementIDs; revisions; owners]
	R23 ISO 19650-1/​-2:2018; R24 ISO 7817-1:2024; R28 ISO 19650-4:2022; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Requirement/​criterion/​delivery reconciliation; office OIR is not client EIR
	RIBA 1;2;3;4;5;6;7
	BIM Manager /​ information management

	IM-02
	Level of information need
	Specify purpose, actors, timing, objects, geometry, data and docs
	[LOIN IDs; object scope; units; files]
	R23 ISO 19650-1/​-2:2018; R24 ISO 7817-1:2024; R28 ISO 19650-4:2022; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Decision-specific review; no automatic stage-to-LOD equivalence
	RIBA 1;2;3;4;5;6;7
	BIM Manager /​ information management

	IM-03
	CDE identity and permitted use
	Use one naming, revision, suitability, state and access mapping
	[ContainerIDs; Rnn; SU; state]
	R23 ISO 19650-1/​-2:2018; R24 ISO 7817-1:2024; R28 ISO 19650-4:2022; R26 ISO 19650-5:2020; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	O3-POL-01 code/​transition checks; acceptance is separate
	RIBA 1;2;3;4;5;6;7
	BIM Manager /​ information management

	IM-04
	Coordinates and exchange profile
	Freeze reference frame, native/​IFC profile and validation
	[CRS per CI-01 and BBM-STD-86; units; IFC 4.0.2.1 Reference View by default, IFC 4.3.2.0 only by recorded approval, authority submissions in the authority's schema (O-DEC-105); IDS 1.0 file per exchange and checker version per BBM-STD-89; BCF 3.0 (BCF 2.1 fallback); authoring build per BBM-STD-91]
	R23 ISO 19650-1/​-2:2018; R24 ISO 7817-1:2024; R28 ISO 19650-4:2022; R36 ISO 16739-1:2024; R37 IDS 1.0; R38 BCF 3.0; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Alignment/​export and receiving-tool samples with exact revisions
	RIBA 1;2;3;4;5;6;7
	BIM Manager /​ information management

	IM-05
	Coordination and interfaces
	Apply intersection, clearance, access and condition-specific rules
	[rule/​envelope IDs and revisions]
	R23 ISO 19650-1/​-2:2018; R24 ISO 7817-1:2024; R28 ISO 19650-4:2022; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	BBM-STD-50 section 3 single rule set and competent design review
	RIBA 1;2;3;4;5;6;7
	BIM Manager /​ information management

	IM-06
	MIDP/​TIDP commitments
	Link criteria/​approvals to stable delivery and exchange milestones
	[DeliveryID; ExchangeID; dates; dependencies]
	R23 ISO 19650-1/​-2:2018; R24 ISO 7817-1:2024; R28 ISO 19650-4:2022; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	LAP reconciles task-team TIDPs and external decision dependencies
	RIBA 1;2;3;4;5;6;7
	BIM Manager /​ information management

	IM-07
	Evidence quality and safety
	Supply current checked geometry/​data/​docs and residual hazards; structured risk records per BBM-STD-88 §4
	[mandatory pass count; issue/​hazard IDs]
	R23 ISO 19650-1/​-2:2018; R24 ISO 7817-1:2024; R28 ISO 19650-4:2022; R27 ISO 19650-6:2025; exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	Independent revision-bound review; unresolved mandatory failures block release
	RIBA 1;2;3;4;5;6;7
	BIM Manager /​ information management

	IM-08
	Asset handover and use
	Supply accepted asset data, O&M, warranties, training and update owner
	[AIR/​profile IDs; assets; receipts]
	R23 ISO 19650-1/​-2:2018; R24 ISO 7817-1:2024; R28 ISO 19650-4:2022; R39 ISO 19650-3:2020; R40 COBie (version per EIR); exact clause/​credit: register ID in BBM-STD-51 §3, clause in BBM-STD-57 Codes table
	FM receiving/​import reconciliation and actual acceptance
	RIBA 1;2;3;4;5;6;7
	BIM Manager /​ information management




B10 · Multidiscipline interfaces
	Interface
	Decision/​check
	Owners
	Evidence

	Structure/​facade/​MEP/​fire
	Loads, movements, fixings, openings, waterproofing and fire barriers
	Competent discipline leads
	CriterionIDs, current calculations/​models/​details and approval/​ChangeIDs

	Architecture/​fire/​security/​access
	Usable accessible and escape routes in normal, emergency and power-failure modes
	Architect/​fire/​access/​security
	Door/​route/​cause-effect matrices and integrated tests

	Civil/​landscape/​utilities
	Levels, flood paths, root/​duct clearances, irrigation supply and corridors
	Civil/​landscape/​utility leads
	Verified levels/​capacity, composite plans and NOCs

	MEP/​supplier/​FM
	Safe access, isolation, replacement route, controls, metering and capacity
	MEP/​supplier/​operator
	Maintenance/​replacement demonstration and commissioning acceptance



Part C · Approvals and authorities register
C0 · Applicability and route control
This is the office master screening list with Abu Dhabi detail and distinct Dubai/other-emirate routes. It does not assert that all rows apply to every project or that a national list can pre-identify every site/use consent. Screen every row; add each plot/use/sector/asset-specific consent; split grouped conditional rows into actual submissions; obtain a written jurisdiction/checklist baseline before the affected activity. Unresolved applicability remains Pending screening, never Approved or N/A by assumption.
Abu Dhabi: apply the ADIBC edition published by DMT and in force at project start (2013 edition at 2026-11-04) [R02]; identify the relevant municipality (Abu Dhabi City, Al Ain or Project), DMT planning functions historically called UPC, ADCD/ADCDA, TAQA Distribution (legacy ADDC/AADC), TAQA Water Solutions (legacy ADSSC/SWS), Abu Dhabi Mobility/ITC and actual serving telecom operator. TAMM, Binaa and e-permitting are submission channels, not approving authorities. DMT's June 2025 Binaa announcement describes phased rollout [R01]; verify actual project eligibility/channel now. Do not duplicate current/legacy applications.
Dubai: establish DM or DDA or PCFC/Trakhees permit jurisdiction and developer/free-zone boundaries. DCD, DEWA, RTA and serving operators remain applicable interfaces. Apply the Dubai Building Code (Decree 45/2021) as amended by DM Administrative Resolution No. 225 of 2024 and every later DM amending resolution in force at permit submission [R17], and Al Sa'fat second edition January 2023 [R18]; each needs an actual adoption record in the BBM-STD-51 §3 register. DM permits that meet the BIM triggers of circulars 9-1-2 and 9-1-3 [R34] need a BIM submission (AP-069); the permit BIM profile is owned by BBM-STD-85 §3. Dubai Law No. 3 of 2026 on the Quality and Safety of Buildings [R33] is an asset-life obligation (periodic inspection and Quality & Safety Certificate for buildings 20 years after completion), screened at G5, not a design-permit rule. PRS does not substitute for a Dubai scheme. Other emirates require a populated local annex.
Decision (BIM Manager, 2026-10-14): Track each actual design approval, construction permission, inspection, connection, completion and occupancy decision separately, with current authority/service, prerequisites, exact required revisions, confirmed review-cycle source and gate. Basis: official service routes [R01, R14, R15, R19, R21, R22] and MIDP dependency method (O-DEC-127).
Every master review-cycle field is verify with authority. Before programme commitment, record current published/written allowance, source/date, calendar, complete-application trigger, stop-clock rules and resubmission allowance. Do not invent fees or durations; internal office review windows are not statutory service times. Documents listed are a submission-content planning checklist; confirm the actual current authority form/profile before applying.

C1 · Abu Dhabi and UAE conditional
ApprovalIDs are stable, not sequential: AP-067/AP-068 (C1) and AP-069 (C2) were added after the first numbering and keep their IDs.
	ApprovalID
	Emirate /​ jurisdiction
	Stage
	Authority
	Submission
	Applicability trigger
	Prerequisite
	Documents /​ drawings required
	Typical review cycle
	Responsible party
	Status
	References

	AP-001
	Abu Dhabi
	Concept/​planning
	DMT municipality
	Jurisdiction, title, plot and affection plan
	All projects; identify ADM/​AAM/​Project jurisdiction
	Client authority and PlotID
	Title/​lease, applicant authority, affection plan and survey
	verify with authority
	Client /​ lead consultant
	Pending screening
	R01;R02

	AP-002
	Abu Dhabi
	Concept/​planning
	DMT planning
	Planning/​master-plan conformity (legacy UPC)
	New development or controls/​use change
	AP-001
	Brief, use, massing, FAR/​GFA/​BUA, setbacks, height and parking/​access
	verify with authority
	Architect /​ planning lead
	Pending screening
	R01;R02

	AP-003
	UAE conditional
	Concept/​planning
	Master developer /​ landlord
	Developer/​landlord design NOC
	Lease/​community or existing-building constraint
	AP-001
	Owner consent, plot/​lease controls and concept/​interfaces
	verify with authority
	Client /​ architect
	Pending screening
	R01;R17

	AP-004
	Abu Dhabi
	Concept/​planning
	Abu Dhabi Civil Defence
	Fire concept/​strategy consultation
	Where local route/​use/​risk requires
	AP-002; occupancy basis
	Fire strategy, occupancy/​escape/​access and hazard/​height classification
	verify with authority
	Fire engineer
	Pending screening
	R03;R30

	AP-005
	Abu Dhabi
	Concept/​planning
	DMT Estidama
	Scheme/​rating and Pearl design registration
	PRS building/​villa/​community applicability
	AP-001; funding/​use
	PQP, scheme/​version/​bulletins and required/​target-credit matrix
	verify with authority
	PQP /​ sustainability lead
	Pending screening
	R05;R06;R07

	AP-006
	Abu Dhabi
	Concept/​planning
	TAQA Distribution
	Water/​power capacity and point-of-connection enquiry
	Network demand/​change; legacy ADDC/​AADC
	AP-001; loads/​demand
	Site plan, load/​demand, proposed substation/​tank/​meter rooms
	verify with authority
	MEP /​ utility coordinator
	Pending screening
	R08

	AP-007
	Abu Dhabi
	Concept/​planning
	TAQA Water Solutions
	Sewer/​reuse capacity and connection enquiry
	Discharge/​reuse; legacy ADSSC/​SWS
	AP-001; discharge basis
	Site/​utility plan, flows/​quality, inverts and connection
	verify with authority
	Civil /​ plumbing lead
	Pending screening
	R08;R09

	AP-008
	Abu Dhabi
	Concept/​planning
	Abu Dhabi Mobility /​ ITC
	TIS scoping and access concept
	Traffic/​access trigger determined by authority
	AP-002; use/​demand
	TIS scope, trip generation, access/​parking/​loading and pedestrians
	verify with authority
	Traffic consultant
	Pending screening
	R10

	AP-009
	Abu Dhabi
	Concept/​planning
	Environment Agency Abu Dhabi
	Environmental screening /​ EIA /​ licence route
	Sensitive site/​impact/​regulated activity
	AP-001; site/​use
	Ecology/​site baseline, process and requested assessment scope
	verify with authority
	Environmental consultant
	Pending screening
	R11

	AP-010
	Abu Dhabi
	Concept/​planning
	DCT Abu Dhabi
	Heritage/​archaeology screening and clearance route
	Heritage setting or archaeological constraints
	AP-001; site screening
	Location, heritage constraints/​impact/​surveys as requested; obtain exact DCT checklist
	verify with authority
	Heritage specialist /​ architect
	Pending screening
	R12;R02

	AP-011
	Abu Dhabi
	Concept/​planning
	ADNOC /​ affected asset operator
	Petroleum asset/​pipeline protection NOC
	Affected asset/​easement/​hazardous interface
	AP-001; verified assets
	Survey, corridor/​crossing, method, risk; confirm exact operating company
	verify with authority
	Civil /​ utility liaison
	Pending screening
	R13

	AP-012
	UAE conditional
	Concept/​planning
	Aviation /​ airport /​ GCAA
	Permanent height/​obstacle screening NOC
	Aviation safeguarding trigger
	AP-001; datum/​height
	Coordinates, permanent maximum height including plant and requested study
	verify with authority
	Aviation specialist /​ architect
	Pending screening
	R31

	AP-013
	Abu Dhabi
	Building permit
	Abu Dhabi Civil Defence
	Fire/​life-safety design approval
	Applicable local design submission
	AP-004; coordinated concept
	Fire plans/​calculations, egress, facade, smoke/​suppression/​alarm and cause-effect/​power
	verify with authority
	Fire engineer /​ MEP
	Pending screening
	R03;R30

	AP-014
	Abu Dhabi
	Building permit
	DMT Estidama
	Pearl Design Rating /​ credit acceptance
	Applicable PRS/​permit-linked sustainability
	AP-005; coordinated design
	Credit evidence, energy/​water models, specifications and drawings
	verify with authority
	PQP
	Pending screening
	R05;R06;R07

	AP-015
	Abu Dhabi
	Building permit
	TAQA Distribution
	Electricity design/​load/​substation NOC
	Supply or network assets affected
	AP-006; coordinated loads
	Loads, SLD, substation/​meter rooms and protection/​connection
	verify with authority
	Electrical consultant
	Pending screening
	R08

	AP-016
	Abu Dhabi
	Building permit
	TAQA Distribution
	Water design/​demand/​connection NOC
	Supply or water assets affected
	AP-006; coordinated demand
	Demand/​storage/​meter calculations, network and backflow details
	verify with authority
	Plumbing /​ civil consultant
	Pending screening
	R08

	AP-017
	Abu Dhabi
	Building permit
	TAQA Water Solutions
	Sewer/​treated-effluent design NOC
	Discharge/​reuse/​network assets
	AP-007; capacity
	Drainage/​reuse flows/​quality, levels, connection and protection
	verify with authority
	Civil /​ plumbing consultant
	Pending screening
	R08;R09

	AP-018
	Abu Dhabi
	Building permit
	e& /​ Etisalat
	Telecom building/​infrastructure design NOC
	Serving operator confirmed; no duplicate assumption
	AP-001; entry points
	Population, rooms/​risers, ducts, power and entry plan; current operator checklist
	verify with authority
	ICT consultant
	Pending screening
	R01

	AP-019
	UAE conditional
	Building permit
	du /​ EITC
	Telecom building/​infrastructure design NOC
	Serving operator/​interface requires du
	AP-001; operator confirmation
	Affection/​site, population, SCS/​GSM floor/​room/​riser and related SLD
	verify with authority
	ICT consultant
	Pending screening
	R14

	AP-020
	Abu Dhabi
	Building permit
	Abu Dhabi Mobility /​ ITC
	TIS approval /​ access and parking agreement
	Required study/​access changes
	AP-008; agreed scope
	TIS, parking/​loading, access/​junction/​pedestrian plans and response matrix
	verify with authority
	Traffic consultant
	Pending screening
	R10

	AP-021
	Abu Dhabi
	Building permit
	DMT municipality /​ roads-drainage
	Road, stormwater and public-realm design NOC
	Municipal network/​ROW affected
	AP-020; utility constraints
	Road/​drainage calculations, levels, catchment/​flood route and public realm
	verify with authority
	Civil /​ landscape leads
	Pending screening
	R01;R02;R10

	AP-022
	Abu Dhabi
	Building permit
	Environment Agency Abu Dhabi
	Environmental licence/​approval and conditions
	As determined by screening
	AP-009; requested studies
	Assessment/​management plans, ecology/​contamination and mitigation/​monitoring
	verify with authority
	Environmental consultant
	Pending screening
	R11

	AP-023
	Abu Dhabi
	Building permit
	DMT municipality
	Building permit /​ coordinated technical acceptance
	Building works; confirm exact portal/​project eligibility
	AP-002; all applicable pre-permit NOCs incl AP-013/​AP-014; appointments/​licences
	Architecture/​structure/​MEP/​civil, code matrix/​calculations, survey/​geotech, NOCs and required BIM/​CAD profile. BIM profile only where the Binaa/​municipality checklist or the appointment requires it; no universal Abu Dhabi building-permit BIM threshold was found; follow R35 where it applies
	verify with authority
	Registered lead consultant
	Pending screening
	R01;R02;R32;R35

	AP-024
	Abu Dhabi
	Building permit
	Gas regulator /​ licensed operator
	Gas/​fuel design approval
	Gas/​fuel proposed; exact authority/​rule to verify
	AP-013; gas source/​use
	Load/​storage/​layout, detection/​shutdown, ventilation/​fire and risk
	verify with authority
	Licensed gas specialist
	Pending screening
	R02;R03

	AP-025
	UAE conditional
	Building permit
	District cooling provider
	Capacity/​connection and design interface acceptance
	District cooling mandated/​selected
	AP-001; HVAC demand
	Capacity, connection/​chamber, hydraulics, metering and access
	verify with authority
	Mechanical consultant /​ client
	Pending screening
	R02;R17

	AP-026
	UAE conditional
	Building permit
	Health /​ education /​ tourism regulator
	Sector use-specific design/​operating approval route
	Healthcare, school, hotel or regulated use
	AP-002; actual regulator identified
	Operational brief, exact sector standard/​version, room/​equipment and safety plans
	verify with authority
	Client /​ sector specialist
	Pending screening
	R12;R02;R17

	AP-027
	UAE conditional
	Building permit
	Security regulator /​ police
	Security/​CCTV design approval
	Site/​use/​security jurisdiction trigger
	Risk basis and exact authority/​profile
	Sensitive security/​coverage/​retention/​access and fire-interface matrix
	verify with authority
	Security consultant
	Pending screening
	R26;R02;R17

	AP-028
	UAE conditional
	Building permit
	Waste /​ public health authority
	Waste, food, pool/​public-health design approval
	Use/​activity triggers
	AP-002; operating brief
	Waste collection/​storage, kitchen/​grease/​exhaust, pool/​public-health as applicable
	verify with authority
	Architect /​ specialist
	Pending screening
	R02;R12;R17

	AP-029
	Abu Dhabi
	Construction
	DMT municipality
	Demolition/​enabling/​excavation/​shoring permit
	Scope-specific early works
	AP-001; relevant design and affected NOCs
	Scope drawings, temporary works, surveys, method/​risk and contractor/​insurance per service
	verify with authority
	Lead consultant /​ contractor
	Pending screening
	R01;R02

	AP-030
	Abu Dhabi
	Construction
	DMT municipality
	Work start notice /​ mobilisation authorisation
	Permitted works ready to start
	AP-023; site/​contractor prerequisites
	Land handover, project-board and start photos plus current service checklist
	verify with authority
	Contractor /​ supervisor
	Pending screening
	R32

	AP-031
	Abu Dhabi
	Construction
	Abu Dhabi Mobility /​ ITC
	Traffic diversion/​road occupation/​work-zone permit
	Road/​path/​traffic affected
	Approved traffic plan and affected consents
	Temporary traffic plan, staging, pedestrian protection and method
	verify with authority
	Contractor /​ traffic engineer
	Pending screening
	R10

	AP-032
	UAE conditional
	Construction
	Aviation /​ airport /​ GCAA
	Crane/​temporary tall-plant obstacle NOC
	Safeguarding/​height trigger
	AP-012; crane positions/​programme
	Maximum tip height/​datum, coordinates, envelope, dates and mitigation
	verify with authority
	Contractor /​ aviation specialist
	Pending screening
	R31

	AP-033
	Abu Dhabi
	Construction
	Asset operators /​ municipality
	Utility crossing/​diversion/​excavation/​protection NOCs
	Works close to services/​ROW
	Relevant AP-011/​015/​016/​017; proven asset locations
	Composite survey, protection/​crossing design, method, PTW and monitoring
	verify with authority
	Contractor /​ utility coordinator
	Pending screening
	R08;R09;R10;R13

	AP-034
	Abu Dhabi
	Construction
	EAD /​ receiving discharge authority
	Dewatering/​discharge/​environmental work consent
	Extraction/​discharge/​contamination/​ecology trigger
	AP-022; agreed recipient/​route
	Dewatering design, water quality/​volume/​point and mitigation/​monitoring
	verify with authority
	Environmental consultant /​ contractor
	Pending screening
	R11;R02

	AP-035
	UAE conditional
	Construction
	Utility operators
	Temporary power/​water connection
	Construction supply needed
	Accepted load/​demand and safe installation
	Temporary SLD/​network, meter/​connection application and safety inspection
	verify with authority
	Contractor /​ utility coordinator
	Pending screening
	R08;R19

	AP-036
	UAE conditional
	Construction
	Civil Defence /​ competent authority
	Facade/​material/​fire-system specialist acceptance
	Product/​shop design approval required
	AP-013 or applicable Dubai fire design approval
	System test scope, certificates, shop design/​calculations and technical submittals
	verify with authority
	Fire contractor /​ supervisor
	Pending screening
	R03;R30

	AP-037
	UAE conditional
	Construction
	du /​ e& serving operator
	Telecom materials/​construction NOC and interim inspection
	Approved telecom design entering installation
	AP-018 or AP-019
	Materials, installation layouts and readiness inspection request
	verify with authority
	ICT contractor /​ supervisor
	Pending screening
	R14;R01

	AP-038
	Abu Dhabi
	Construction
	DMT municipality /​ competent authority
	Mandatory structural/​MEP/​stage inspections
	Permit inspection/​hold-point schedule
	AP-023; accepted ITP
	Inspection requests, approved drawings, test reports and stage records
	verify with authority
	Contractor /​ supervisor
	Pending screening
	R02;R01

	AP-039
	UAE conditional
	Construction
	Original approving authorities
	Amended design/​permit/​NOC resubmission
	Changed scope/​drawings or expired/​invalid consent
	ChangeID and affected impact assessment
	Revised calculations/​drawings, comparison, original approvals and response matrix
	verify with authority
	Lead consultant /​ discipline leads
	Pending screening
	R01;R14;R17

	AP-040
	Abu Dhabi
	Construction
	DCT Abu Dhabi
	Heritage works/​chance-find clearance
	Discovery or heritage-condition trigger
	AP-010 conditions; protect affected works
	Location/​find record, specialist assessment and written restart clearance
	verify with authority
	Contractor /​ heritage specialist
	Pending screening
	R12;R02

	AP-041
	Abu Dhabi
	Completion/​occupancy
	Abu Dhabi Civil Defence
	Final fire inspection/​completion clearance
	Installed fire systems ready
	AP-013;AP-036; current approved revisions
	As-builts, system tests/​cause-effect, facade/​product records, commissioning/​maintenance
	verify with authority
	Fire contractor /​ consultant
	Pending screening
	R03;R30

	AP-042
	Abu Dhabi
	Completion/​occupancy
	TAQA Distribution
	Electricity final inspection/​energisation and water connection
	Permanent supply ready
	AP-015;AP-016; operator conditions
	As-builts, tests, approved loads/​SLD, meter/​connection readiness and network release
	verify with authority
	MEP contractor /​ consultant
	Pending screening
	R08

	AP-043
	Abu Dhabi
	Completion/​occupancy
	TAQA Water Solutions
	Sewer/​reuse final inspection and connection acceptance
	New/​altered network connection
	AP-017; approved installed works
	As-builts, tests/​CCTV where required, connection/​discharge and asset handover
	verify with authority
	Civil contractor /​ consultant
	Pending screening
	R08;R09

	AP-044
	UAE conditional
	Completion/​occupancy
	du /​ e& serving operator
	Telecom final inspection, room handover and service availability
	Permanent telecom/​infrastructure ready
	AP-037; approved design/​readiness
	Tests/​as-builts, rooms/​containment handover and written availability
	verify with authority
	ICT contractor /​ client
	Pending screening
	R14;R01

	AP-045
	Abu Dhabi
	Completion/​occupancy
	DMT Estidama
	Pearl Construction Rating /​ credit closeout
	Applicable PRS scope
	AP-014; construction evidence
	Credit/​procurement/​site evidence, changes, commissioning and PQP closeout
	verify with authority
	PQP /​ contractor
	Pending screening
	R05;R07

	AP-046
	UAE conditional
	Completion/​occupancy
	Relevant specialist regulators
	Lift/​gas/​sector/​security/​environment final clearance
	Applicable system/​regulated use; split actual submissions
	Relevant design approvals and completed installation
	Witnessed tests, certificates/​licences, as-builts and operating/​safety arrangements
	verify with authority
	Client /​ specialists /​ contractor
	Pending screening
	R02;R03;R11;R12;R26

	AP-047
	Abu Dhabi
	Completion/​occupancy
	DMT municipality
	Building completion certificate
	Permitted works and inspections complete
	AP-038/​AP-039; all applicable completion NOCs
	Approved/​as-built package, supervision/​tests, fire/​utility/​sustainability clearance and checklist
	verify with authority
	Supervising consultant /​ contractor
	Pending screening
	R02;R15

	AP-048
	Abu Dhabi
	Completion/​occupancy
	DMT municipality
	Applicable initial/​full/​temporary occupancy certificate
	Actual new/​existing/​phased-use category confirmed
	AP-047 and category-specific prerequisites confirmed by municipality
	Owner application, structural/​fire/​gas/​lift/​MEP safety and temporary-occupation boundaries if relevant
	verify with authority
	Owner /​ licensed consultant
	Pending screening
	R15;R16

	AP-049
	Abu Dhabi
	Operation/​renewal
	DMT municipality /​ sector regulators
	Occupancy/​operating licence renewal and conditions
	Before actual expiry or material use change
	AP-048; actual certificate category/​validity
	Current safety/​maintenance reports, operating licences and corrective actions
	verify with authority
	Owner /​ FM
	Pending screening
	R15;R16

	AP-067
	UAE conditional
	Concept/​planning
	Rail /​ port /​ coastal /​ defence asset owner
	Special infrastructure/​safeguarding/​waterfront NOC
	Protected strategic asset/​interface
	Location, corridor and competent asset owner
	Crossing/​marine/​safeguarding studies and exact written checklist
	verify with authority
	Client /​ civil specialist
	Pending screening
	R02;R17;R31

	AP-068
	UAE conditional
	Construction
	Competent municipality /​ landlord /​ Civil Defence
	Fit-out/​change-of-use/​signage/​alteration permit
	Work/​use differs from base-build approval
	Existing completion/​occupancy; landlord and sector/​fire consents
	Existing/​proposed plans, loads/​population/​fire/​MEP changes and current service checklists
	verify with authority
	Tenant/​client /​ consultant
	Pending screening
	R02;R03;R17;R21;R22



C2 · Dubai variations
	ApprovalID
	Emirate /​ jurisdiction
	Stage
	Authority
	Submission
	Applicability trigger
	Prerequisite
	Documents /​ drawings required
	Typical review cycle
	Responsible party
	Status
	References

	AP-050
	Dubai - DM jurisdiction
	Concept/​planning
	Dubai Municipality
	Planning/​plot/​demarcation and concept route
	DM planning jurisdiction
	Client authority; plot/​zone confirmation
	Title/​site/​affection plan, land use, massing/​GFA, height and parking
	verify with authority
	Architect /​ client
	Pending screening
	R17

	AP-051
	Dubai - DDA jurisdiction
	Concept/​planning
	Dubai Development Authority
	DDA planning and final design approval route
	DDA jurisdiction confirmed
	Developer/​master-plan/​plot conditions
	DDA design package, planning controls, coordinated disciplines and NOCs
	verify with authority
	Lead consultant
	Pending screening
	R21

	AP-052
	Dubai - Trakhees jurisdiction
	Concept/​planning
	PCFC /​ Trakhees
	CED/​EHS planning and design route
	Trakhees jurisdiction confirmed
	Developer/​plot controls; active CED/​EHS route
	Design/​environment/​health/​safety/​green-building package and accreditation per current checklist
	verify with authority
	Lead consultant /​ EHS specialist
	Pending screening
	R22

	AP-053
	Dubai
	Building permit
	Dubai Civil Defence
	Fire/​facade/​life-safety design approval
	Applicable Dubai fire submission
	AP-050/​051/​052 as relevant; fire strategy
	DCD plans/​calculations, facade evidence and systems/​cause-effect
	verify with authority
	Fire engineer /​ MEP
	Pending screening
	R03

	AP-054
	Dubai
	Building permit
	DEWA
	Electricity and water building NOCs
	DEWA network/​service jurisdiction
	Plot, demand/​load and coordinated layout
	Site, SLD/​loads/​substation/​water design per current checklist
	verify with authority
	MEP consultant
	Pending screening
	R19

	AP-055
	Dubai
	Building permit
	RTA
	TIS/​access/​ROW/​rail protection NOCs
	Traffic/​access/​ROW/​rail trigger
	Confirmed assets/​location, demand and study scope
	Traffic/​access study and ROW/​crossing/​rail design, method/​risk as requested
	verify with authority
	Traffic /​ civil consultant
	Pending screening
	R20

	AP-056
	Dubai
	Building permit
	DM /​ sewer-drainage operator
	Sewer/​stormwater/​public-health/​waste design clearance
	Network/​health/​use trigger
	Plot/​service capacity and discharge basis
	Civil/​drainage plans/​calculations, levels, food/​pool/​waste strategy as applicable
	verify with authority
	Civil /​ specialist consultants
	Pending screening
	R17

	AP-057
	Dubai - competent jurisdiction
	Building permit
	DM /​ DDA /​ Trakhees sustainability
	Al Sa'fat /​ jurisdiction green-building acceptance
	Exact jurisdiction scheme confirmed
	AP-050/​051/​052; applicable scheme
	Energy/​water/​envelope evidence and jurisdiction forms; PRS is not a substitute
	verify with authority
	Sustainability lead
	Pending screening
	R18;R21;R22

	AP-058
	Dubai - DM jurisdiction
	Building permit
	Dubai Municipality
	DM building permit
	DM is competent permit authority
	AP-050 and all applicable fire/​utility/​traffic/​sustainability NOCs
	Architecture/​structure/​MEP/​calculations, survey/​geotech and consents; where circular 9-1-2 or 9-1-3 is triggered, the BIM model and model-extracted drawings (AP-069)
	verify with authority
	Registered consultant
	Pending screening
	R17;R34

	AP-069
	Dubai - DM jurisdiction
	Building permit
	Dubai Municipality (Building Regulation and Permits Agency)
	BIM model submission with the building permit (Open BIM, IFC)
	Circular 9-1-2 (from 1 Jan 2024): over 20 floors (architectural) /​ 40 floors (structural), over 20,000 m² (architectural) /​ 30,000 m² (structural), specialised buildings such as hospitals and universities, government projects except utility projects. Circular 9-1-3 (effective 1 Apr 2026): new buildings above G+12 or of 15,000 m² or more (architectural and structural); alterations to BIM-licensed buildings that add or remove floors, add 1,500 m² or more, fully redesign, change the main use or relocate on the plot need BIM with the application; other alterations need a final BIM model before the completion certificate
	AP-050; BEP exchange profile; IFC schema and export setup stated in the current Dubai BIM Standard (buildindubai.gov.ae/​bim), checked at project start and recorded in the BEP
	Zipped openBIM IFC within the portal upload limit; drawings extracted from the model and submitted with it; attributes per the Model Attribute Matrix issued with the current Dubai BIM Standard; IFC schema/​IDS check record before upload
	verify with authority
	Registered consultant /​ BIM Manager
	Pending screening
	R17;R34

	AP-059
	Dubai - DDA jurisdiction
	Building permit
	Dubai Development Authority
	DDA final building permit
	DDA is competent permit authority
	AP-051 final design approval; applicable NOCs; demarcation before site activity
	DDA application and current consultant/​contractor/​approval evidence
	verify with authority
	Contractor (applicant) /​ registered consultant (design coordination)
	Pending screening
	R21

	AP-060
	Dubai - Trakhees jurisdiction
	Building permit
	PCFC /​ Trakhees
	Trakhees building permit /​ EHS NOC
	Trakhees is competent permit authority
	AP-052; applicable CED/​EHS/​NOC prerequisites
	Active CED/​EHS permit package, accepted design/​accreditation
	verify with authority
	Registered consultant
	Pending screening
	R22

	AP-061
	Dubai
	Construction
	DM /​ DDA /​ Trakhees competent authority
	Early works/​construction permits, inspections and amendments
	Actual jurisdiction and scope/​hold points
	AP-058 or AP-059 or AP-060; exact activity permission
	Traffic/​utility/​crane/​early works consents, inspections/​products and changed-scope approvals
	verify with authority
	Contractor /​ supervisor
	Pending screening
	R17;R20;R21;R22

	AP-062
	Dubai
	Completion/​occupancy
	DCD /​ DEWA /​ relevant operators
	Fire, utility and specialist final clearances
	Installation ready for authority inspections
	Relevant Dubai design approvals and stage inspections
	As-builts, tests/​commissioning, fire/​utilities, specialist and operator handover
	verify with authority
	Contractor /​ consultant
	Pending screening
	R03;R19

	AP-063
	Dubai - competent jurisdiction
	Completion/​occupancy
	DM /​ DDA /​ Trakhees competent authority
	Completion/​occupancy/​operating release route
	Exact jurisdiction/​use category
	AP-062; all applicable closeouts
	Current completion checklist, certificates, sustainability/​as-builts and sector licence; verify separate occupancy route; for a DM BIM-licensed alteration, the final BIM model (AP-069)
	verify with authority
	Owner /​ supervising consultant
	Pending screening
	R17;R18;R21;R22;R33;R34

	AP-070
	Dubai - all jurisdictions, including free zones and special development areas
	Use/​renewal
	Dubai Municipality (Building Regulation and Permits Agency)
	Building Quality and Safety Certificate (Build in Dubai e-service)
	Building completed 20 or more years ago, on DM notice (phased: multi-storey buildings over 40 years first)
	Owner appoints an engineering office licensed in Dubai with classification matching the building height; Civil Defence and SIRA compliance certificates
	Technical report against the DM technical checklist (structure, external cladding, windows/​doors/​guards, external and common-area MEP, Civil Defence, SIRA) with laboratory tests as needed; where defects exist, remediation methods, material specifications, agreed duration and owner undertaking, then remediation records; procedure in BBM-STD-75 §7
	DM review, permit to start remediation, inspection; valid 10 years (under 40 years since completion) or 5 years (40+), renewal in the last 90 days before expiry
	Owner /​ appointed engineering office
	Pending screening
	R33;R42



C3 · Other-emirate route annex
	ApprovalID
	Emirate /​ jurisdiction
	Stage
	Authority
	Submission
	Applicability trigger
	Prerequisite
	Documents /​ drawings required
	Typical review cycle
	Responsible party
	Status
	References

	AP-064
	Other emirates - Sharjah
	Concept/​planning
	Sharjah competent authorities
	Local permit/​NOC/​utility/​occupancy route screening
	Sharjah site; not copied AD/​Dubai rules
	Plot/​use/​free-zone jurisdiction
	Confirm planning/​municipality, Civil Defence, SEWA, roads, telecom, sewer/​environment/​sector routes; split stage rows
	verify with authority
	Lead consultant
	Pending screening
	R29

	AP-065
	Other emirates - Ajman/​UAQ/​Fujairah
	Concept/​planning
	Local municipality /​ free-zone authority
	Local permit/​NOC/​utility/​occupancy route screening
	Project in named emirate
	Plot/​use/​free-zone jurisdiction
	Confirm building/​planning, Civil Defence, EtihadWE or serving utility, sewer/​roads/​telecom/​environment/​sector; split rows
	verify with authority
	Lead consultant
	Pending screening
	R29

	AP-066
	Other emirates - Ras Al Khaimah
	Concept/​planning
	RAK competent authorities
	Local permit/​NOC /​ Barjeel screening
	RAK site and actual jurisdiction
	Plot/​use/​municipality or free zone
	Obtain current Barjeel code/​edition/​applicability and planning/​building/​fire/​utilities/​roads/​telecom/​environment/​occupancy routes; split stage rows
	verify with authority
	Lead consultant
	Pending screening
	R29




C4 · Actual submission tracker and status rules
For each actual submission maintain: ApprovalID, ParentApprovalID when split, jurisdiction, stage, actual authority/service/version/URL/date, applicability decision/evidence, prerequisite IDs, document/drawing IDs/revisions, applicant, responsible person, planned/actual submission dates, verified review basis and target response, receipt/application number, review comments/conditions with owners/dates, decision date/record, validity/expiry, revalidation trigger, MIDP DeliveryID/ExchangeID, allowed next activity and gate checker.
The canonical approval-status vocabulary is the BBM-STD-57 §2/§4 set (O-DEC-110; O-DEC-140): Unverified, Planned, Submitted, Conditionally approved, Approved, Rejected, Expired. "Not applicable" is an applicability decision, not a status. The tracker's working statuses map to it in BBM-STD-93 §7: Pending screening (= Unverified), Not started and In preparation (= Planned), Submitted and Under review (= Submitted), Revise/resubmit and Rejected (= Rejected), Approved with conditions (= Conditionally approved), Approved (= Approved), Expired and Superseded (= Expired; Superseded is also kept as a record flag); Not applicable is an applicability decision with recorded reason and authority. N/A needs signed applicability evidence. Submitted needs actual receipt. Approval needs the authority's exact decision and scope, not a consultant recommendation. Conditional approval does not release an activity until the relevant conditions are checked closed; confirm scope and expiry. Changed drawings/scope trigger affected NOC/permit review and resubmission where required. Preserve every prior application and decision.
Completion and occupancy are separate checks. DMT Administrative Decision No. 1 of 2024 [R15] and the 5 August 2026 notice [R16] establish an active occupancy-certification framework. Record actual category, applicability, permitted areas/use, conditions and expiry. Partial/temporary occupation needs approved fire/utility/escape/separation arrangements and the actual certificate for that boundary. Handover, energisation, completion or a pending application alone do not establish occupancy permission. Verify existing-building exceptions and renewal timing for the actual case; no universal certificate validity is assigned here.
C5 · Stage, authority and release gates
[image: ]
Indicative stage-to-authority-to-gate path. Confirm actual sequence/parallel reviews; return changed scope to affected approvals.
These BoD gates G0–G5 are one of three gate families (O-DEC-109): office stage gates (Manual §2.1), BoD gates G0–G5 (here) and authority gates (BBM-STD-57 §4). The mapping is in BBM-STD-93 §6: G1 = Concept/planning, G2 = Permit/final design, G3 = Construction activity, G4 = Completion/operation; G0 and G5 have no authority-gate equivalent. Gate outcomes are letters A/B/C (O-DEC-107).
	Gate
	Evidence /​ release condition
	Responsible check

	G0 Basis
	Brief/​OPR, plot/​survey, jurisdiction, adopted-code and screening baseline; any bounded study limitations explicit
	Lead consultant/​client and competent discipline authorities

	G1 Concept/​planning
	Applicable planning/​developer/​traffic/​environment/​heritage/​utility constraints and concept decisions current
	Lead consultant and actual authority decisions

	G2 Permit/​start activity
	Required design approvals/​NOCs, valid relevant building/​early-works permission and all conditions for exact next activity closed
	Permit applicant, supervisor and contractor verify authority evidence

	G3 Construction
	Approved designs/​products, stage inspections, site/​utility/​traffic consents and amended approvals before covering/​releasing work
	Supervisor, inspector and competent authority

	G4 Completion/​occupancy
	Final tests/​as-builts/​fire/​utilities/​sustainability/​sector clearances, completion and applicable occupancy/​operating decisions
	Supervisor/​owner/​operator; authorities grant their own permissions

	G5 Use/​renewal
	Actual certificate/​maintenance/​inspection renewals and operating performance/​actions current; in Dubai, Law No. 3 of 2026 periodic inspection and Building Quality and Safety Certificate once the building is 20 years from completion, procedure in DM circular 11-9-1 of 2026 (AP-070) [R33; R42]
	Owner/​FM and competent municipality/​sector regulator



Part D · Decisions, assumptions, deviations and MIDP links
D1 · Option appraisal and decision log
Safety, statutory requirements and mandatory client outcomes are vetoes. Compare viable options on equal scope: performance, whole-life cost, constructability, programme, maintenance, environmental impact and evidence confidence. Set any scoring weights/normalisation before scoring and preserve raw values; a preferred score cannot waive a veto.
	DecisionID/​date/​stage
	Requirement/​purpose/​options
	Comparable measures/​evidence
	Required LOIN/​revision
	Selection/​rationale/​risk
	Designer/​checker/​authoriser
	Affected criteria/​approvals/​ChangeID

	DEC-[nnn] /​ [date/​Sx]
	[RequirementIDs; baseline and alternatives]
	[Values/​units/​boundary, source/​calculation revisions and veto results]
	[Purpose, actors, timing, objects, geometry/​data/​docs]
	[Chosen option, trade-offs, uncertainty and review trigger]
	[Actual role-holder IDs and decision record]
	[Criterion/​AP/​Delivery/​ExchangeIDs; ChangeID]



D2 · Assumptions and uncertainty register
	AssumptionID
	Assumed value/​unit/​range
	Source/​confidence/​why needed
	Affected decision/​consequence
	Validation action/​owner/​due milestone
	Disposition/​expiry/​approval evidence

	ASM-[nnn]
	[Value, units and uncertainty]
	[Evidence reference or explicit unsupported assumption]
	[CriterionIDs and safety/​cost/​permit impact]
	[Test, role-holder, date/​ExchangeID]
	[Pending/​validated/​replaced/​rejected; exact record]



Assumptions are allowed only for a bounded study purpose with risk/limitations visible. Resolve critical occupancy, escape, stability, utilities or survey assumptions before affected reliance. A due date passing never validates an assumption. Replace assumptions through ChangeID, retaining original records and affected revisions.
D3 · Deviation/derogation register
	DeviationID/​ChangeID
	Requirement/​adopted clause
	Required vs proposed value/​reason
	Impact/​compensation/​tests
	Required consenting authority
	Decision/​scope/​expiry/​conditions
	Outputs/​closure

	DEV-[nnn] /​ CHG-[nnn]
	[Register ID/​CriterionID; statutory/​client/​office class]
	[Same units and explicit difference]
	[Safety/​access/​performance/​cost/​programme/​operation]
	[Competent designer; client for client target; AHJ for law; office owner for office rule]
	[Pending/​accepted/​refused; actual written consent]
	[Calculations/​drawings/​models/​permits and completed actions]



BIM Manager consent cannot waive technical law; client consent cannot waive statutory limits. Alternative solutions need competent design justification and actual statutory approval where required. Until consent/conditions are evidenced, status remains Deviation, blocking affected release. A lawful accepted alternative becomes the new documented requirement only after controlled baseline revision/recheck; retain the original requirement and consent lineage.
D4 · Approval tracker linked to delivery milestones
	ApprovalID/​submission rev
	MIDP DeliveryID/​ExchangeID/​TIDP row
	Predecessor/​recipient/​decision
	Planned submit/​review basis/​response
	Actual receipt/​comments/​decision
	Conditions/​expiry/​revalidation
	Gate/​activity/​ChangeID

	[AP-ID; manifest revision]
	[Stable IDs and baseline revisions]
	[Approval/​evidence IDs and actual authority]
	[Real dates; confirmed allowance/​resubmission]
	[Receipt number/​date; decision/​status]
	[Owner/​due/​evidence; validity]
	[Permitted activity, checker/​date and lineage]



1.  Work back from each required decision/activity: production, L1 discipline check, L2 coordination, L3 technical committee as applicable, corrections, authorisation, external review/resubmission and recipient acceptance are separate allowances.
2.  Task leads commit TIDPs; LAP reconciles MIDP. Authority coordinator provides confirmed external dependencies. One ChangeID updates affected design, approval, procurement, temporary works and handover commitments.
3.  Retain revised dates/baselines, notices and acknowledgements. Upload, meeting note or dashboard colour is not receipt or approval evidence.
D5 · Completed synthetic example (training only)
Values below are fictitious client/manufacturer requirements, not UAE code limits, actual project evidence or authority approvals.
	Trace
	Synthetic record
	Decision /​ consequence

	OPR-SYN-01 -> ME-21 /​ IM-05
	Manufacturer SYN-MFR-01 R01 requires 600 mm AHU withdrawal clearance (same synthetic requirement as TIDP V0.3); model SYN-ME R02 provides 520 mm
	Shortfall 80 mm; Deviation. No averaging with other criteria

	DEC-SYN-01 /​ LOIN-SYN-01
	Option A moves partition to provide 650 mm; option B changes unit but supplier dimensions remain unverified. Need geometry, dimensional data and replacement-sequence drawing
	Select A subject to architecture/​fire/​access review; B is not validated

	CHG-SYN-01
	MEP/​architect agree revised model; fire/​access check route; independent check confirms 650 mm against unchanged 600 mm requirement
	ME-21 may become Compliant for RIBA 3 only after current evidence accepted; no permit is fabricated

	MIDP-SYN-01 /​ actual project AP-ID
	Revised documents and approval-impact assessment linked to ExchangeID
	Construction remains blocked until actual applicable permissions and conditions are satisfied

	RIBA 6/​7
	RIBA 3 geometry does not prove installed access or operating performance
	Witness replacement/​maintenance access and FM acceptance; keep each stage's evidence



Part E · Measurement, acceptance and sign-off
E1 · Stage scorecard and release rule
The workbook expands each Part B criterion into every listed stage. CriterionID + stage + location/object scope is the project key; allocate unique suffixes for split locations. Retain stage history and baseline revisions. Applicability begins Pending screening.
Evidence statuses are Compliant, Deviation, Pending evidence. Applicability is separate: Required, Not applicable, Pending screening. N/A needs reason, owner, checker/date and current decision evidence, and never counts as compliant. Blank adoption/clause, target/unit, result, evidence revision or competent check means Pending evidence regardless of a typed Compliant label. Numeric targets/results are typed numbers in the project workbook; categorical checks use explicit categories and documented comparison.
	Stage/​gate/​scope
	Required N
	Compliant C
	Deviation D
	Pending P
	Approved N/​A
	Unscreened U
	Coverage /​ decision

	[Sx; ExchangeID; zone]
	[Required rows]
	[Current supported pass rows]
	[Required failed rows]
	[Required without supported pass/​fail]
	[Valid exclusions]
	[Pending screening]
	C/​N only if N>0; otherwise N/​A with scope approval. Release requires U=0, D=0, P=0, valid N/​A bases and required authority gates closed



Do not combine stages into a misleading percentage. Show scope, date, denominator, raw counts, failed criteria and source revisions. If optional/aspirational targets are added, report them separately; they cannot offset mandatory failure. Spreadsheet completeness checks do not verify source authenticity, engineering comparison or statutory applicability; competent reviewers sign the actual evidence.
E2 · Evidence record
	Criterion/​stage/​scope
	Target/​unit/​comparison
	Actual result
	Adoption/​clause/​evidence revision
	Method/​uncertainty/​outcome
	Checker/​date/​technical approver
	Approval and delivery links

	[ID; Sx; zone/​object population]
	[Mandatory flag; min/​max/​range/​exact/​category and value]
	[Typed measurement/​calculation or explicit category]
	[BBM-STD-51 §3 register ID; exact verified clause; calc/​drawing/​model/​test IDs+revisions]
	[Conditions, tolerance/​uncertainty, pass/​fail reason]
	[Distinct competent checker; signature/​date]
	[AP/​DEC/​DEV/​ASM/​CHG; Delivery/​ExchangeIDs]



E3 · Sign-off record per stage and revision
	Function
	Required sign-off /​ evidence

	Discipline preparer
	[Criteria, sources and evidence complete; scope/​revision; role-holder signature/​date]

	Independent competent checker
	[Calculations, units, comparison, safety/​interfaces and exceptions; signature/​date]

	Lead consultant /​ technical committee
	[Cross-discipline basis, residual risks and approved stage baseline; signature/​date]

	Authority coordinator
	[Applicability, actual consents, conditions, scope/​expiry and next activity checked; register revision/​date]

	LAP /​ information management
	[MIDP/​TIDP/​LOIN, manifest, permitted use and access; signature/​date]

	Client /​ asset owner /​ FM
	[Requirements/​operational acceptance, limitations, residual actions and owners; decision/​date]

	Release authoriser
	[Gate, permitted use, exact revisions, open-gap list and release record]

	Statutory decisions
	[Separate actual authority records; consultant signatures do not substitute]



E4 · Acceptance criteria and handover
•  Verified client/plot/use/phasing data and code-adoption baseline; unsupported inputs visibly bounded.
•  Every mandatory criterion has project target/unit, verified source/clause, method, stage, owner and current independent evidence; all unresolved mandatory failures block affected release.
•  No unexplained pending screening/N/A at release. Required authority decisions, conditions, permitted activity, validity and changed-scope reviews are evidenced.
•  Options, assumptions, deviations and interfaces trace to current calculations/drawings/models and one ChangeID propagated to MIDP/TIDPs.
•  RIBA 6 evidence includes approved design/as-built reconciliation, inspections, witnessed integrated fire/MEP and fail-state tests, calibration records, commissioning/seasonal-test plan, accepted O&M/asset data, warranties, operator training and demonstrated capability, required maintenance contracts/licences. Record residual/seasonal owner and due trigger; do not carry a non-waivable safety condition into occupancy.
•  FM tests import/use and reconciles asset information; actual receipt/acceptance names the scope/revision. At RIBA 7 compare monitored energy/water/comfort/system operation with approved targets, investigate differences and update controlled asset information.
•  Retain immutable released manifests, superseded decisions and actual authority certificates in the CDE. Restrict sensitive security/identity records; link controlled evidence rather than copying it into unrestricted reports.
Research coverage and boundaries
Method: requirements/conditions -> assumptions -> options -> discipline criteria -> interfaces -> current evidence -> commissioning/operation; no TBP product marketing copied. Sources are tagged in the References below and the edition register (BBM-STD-51 §3). Controls and the synthetic example are template methods, not claimed project compliance.
Controls retained from the office set: terminology/requirements; CDE vs acceptance; one naming grammar; purpose-led LOIN; single coordination rules; MIDP/TIDP ownership; survey certainty; correct RIBA stage names; appointment authority; model-vs-code safety distinction. No new tolerance or naming policy is created.
Conditional heritage, sector, gas, security, district-cooling and other-emirate entries are screening prompts; checklists, clauses and applicability come from the competent authority. Research accessed 16 October 2026; UAE entries rechecked 4 November 2026. Blank fields are required project inputs.

References · official publications and routes
Publication edition/date is given where verified; live undated pages use the access date. RESEARCH.md S01/S02/S03/S04/S05/S06/S07/S19/S21 supplies the prior information-management basis. Editions and adoption are held once in the BBM-STD-51 §3 register (O-DEC-111); this table keeps the BoD reference IDs used in the criteria. No technical clause number is invented from an abstract; office decisions are local choices.
	RefID
	Register ID (BBM-STD-51 §3)
	Title /​ service
	Official publisher
	Edition /​ date
	Official URL
	Applicability boundary
	Access date

	R01
	—
	Binaa Construction Permits Platform launch
	DMT
	18 June 2025; phased rollout
	https:/​/​www.dmt.gov.ae/​en/​Media-Centre/​News/​Binaa-Construction-Permits-Platform-Launched
	Confirm actual eligibility/​channel; TAMM and Binaa are channels, not authorities
	2026-10-16

	R02
	ED-ADIBC
	Abu Dhabi International Codes: ADIBC, ADIECC, ADIFGC, ADIMC, ADIPSDC, ADIPMC
	DMT
	ADIBC edition published by DMT and in force at project start; 2013 edition (Executive Council Resolution 7C 26/​2013, effective 1 October 2013) is the latest DMT publishes at 2026-11-04
	https:/​/​www.dmt.gov.ae/​-/​media/​Project/​DMT/​DMT/​Codes/​3-ADIMC-2013_1-12-2013.pdf
	Obtain adopted volumes, referenced-standard editions and local amendments; record in BBM-STD-51 §3
	2026-11-04

	R03
	ED-UAE-FLS
	UAE Fire and Life Safety Code of Practice
	UAE Ministry of Interior, General Command of Civil Defence (published on the Dubai Civil Defence portal)
	September 2018 edition; no later national edition found
	https:/​/​www.dcd.gov.ae/​portal/​preventive-safety/​uae-fire-and-life-safety-code-of-practice.jsp
	Edition plus the emirate authority's amendments (DCD, ADCDA) current at project start, recorded in the BEP; confirm exact clauses
	2026-11-04

	R04
	—
	Abu Dhabi International Accessibility Standards
	DMT
	Official hosted edition; date/​current amendments to verify
	https:/​/​www.dmt.gov.ae/​-/​media/​Project/​DMT/​DMT/​Codes/​3-ADAccessStd_bookmarked.pdf
	PDF title verified; confirm current accessibility/​Sahel applicability
	2026-10-16

	R05
	ED-ESTIDAMA
	Pearl Building Rating System: Design and Construction
	UPC /​ DMT
	Version 1.0, April 2010; official cover verified
	https:/​/​www.dmt.gov.ae/​-/​media/​Project/​DMT/​DMT/​E-Library/​0001-Manuals/​PBRS/​PBRS-Version-10.pdf
	Select building/​villa/​community scheme; verify current bulletins/​credits
	2026-10-16

	R06
	ED-ESTIDAMA
	Estidama Information Bulletin 3: buildings requiring PBRS
	UPC /​ DMT
	Version 1.0, 2 February 2011
	https:/​/​pages.dmt.gov.ae/​-/​media/​499659DE51C34B118B94DCEFD5384F87.ashx?download=1
	Historical scope list; superseded by R07 for minimum ratings
	2026-11-04

	R07
	ED-ESTIDAMA
	Sustainable green building implementation
	Abu Dhabi City Municipality
	8 January 2025
	https:/​/​www.dmt.gov.ae/​en/​adm/​Media-Centre/​News/​08Jan2025
	Building-permit condition: minimum 1 Pearl private, 2 Pearl government-funded; municipality implements Estidama design/​construction stages
	2026-11-04

	R08
	—
	New unified distribution company and group brands
	TAQA
	16 September 2024; distribution transition January 2025
	https:/​/​taqa-ws.com/​news/​announcements/​taqa-announces-new-unified-customer-facing-distribution-company-and-launches-new-brands-for-its-group-companies/​
	TAQA Distribution replaces ADDC/​AADC; Water Solutions replaces SWS; Transmission replaces TRANSCO
	2026-10-16

	R09
	—
	Wastewater operator services
	TAQA Water Solutions
	Live official site; undated
	https:/​/​taqa-ws.com/​
	ADSSC/​SWS are legacy aliases; exact checklist to verify
	2026-10-16

	R10
	—
	Digital services: TIS and traffic detour
	Abu Dhabi Mobility /​ ITC
	Live official catalogue; undated
	https:/​/​admobility.gov.ae/​en/​digital-services
	Confirm traffic/​access and municipal-road interfaces
	2026-10-16

	R11
	—
	Environmental Assessment and Licensing executive regulation
	EAD
	8 December 2022 publication notice
	https:/​/​www.ead.gov.ae/​en/​Media-Centre/​News/​Executive-Regulations-for-Environmental-Assessment
	EAD determines environmental screening/​licence/​assessment requirements
	2026-10-16

	R12
	—
	Service catalogue: hotel plan approval and licensing
	DCT Abu Dhabi
	Live official catalogue; undated
	https:/​/​dct.gov.ae/​en/​media.centre/​news/​service.card.aspx
	Tourism source; heritage-specific checklist unverified: obtain written DCT route
	2026-10-16

	R13
	—
	Onshore Pipelines Construction Specification AGES-SP-10-003
	ADNOC
	Revision 1; 2021 public repository
	https:/​/​www.adnoc.ae/​-/​media/​adnoc-v2/​files/​specs/​2021/​engineering-standards-and-specifications-october14th/​onshore-pipelines-contruction-spec.ashx
	Asset/​corridor NOC principle, not a universal building rule
	2026-10-16

	R14
	—
	Telecom NOC: design, construction, materials and inspection
	du /​ EITC
	Live official service; undated
	https:/​/​www.du.ae/​no-objection-certificate
	Multiple TDRA versions mentioned: obtain one applicable current profile
	2026-10-16

	R15
	—
	Buildings Occupancy Certification System
	DMT
	Administrative Decision No. 1 of 2024
	https:/​/​pages.dmt.gov.ae/​-/​media/​0E6A6EEBFFFF4FA68DC6868F0AE85DD0.ashx
	Confirm actual category, phased applicability, validity and exceptions
	2026-10-16

	R16
	—
	Occupancy-certificate implementation notice
	DMT
	5 August 2026
	https:/​/​www.dmt.gov.ae/​ar-AE/​Media-Centre/​News/​DMT-Grants-Grace-Period-to-Comply-with-Occupancy-Certificate-Rules
	Current issuance/​renewal screening; completion alone does not establish occupancy permission
	2026-10-16

	R17
	ED-DBC
	Dubai Building Code
	Dubai Municipality
	DBC (Decree 45/​2021) as amended by DM Administrative Resolution No. 225 of 2024 (13 August 2024) "amending some building specifications in the DBC"
	https:/​/​www.dm.gov.ae/​?p=352286
	Apply the DBC plus all DM amending resolutions in force at permit submission; record in BBM-STD-51 §3
	2026-11-04

	R18
	ED-ALSAFAT
	Al Sa'fat - Dubai Green Building System
	Dubai Municipality
	Second edition, January 2023
	https:/​/​www.dm.gov.ae/​municipality-business/​al-safat-dubai-green-building-system/​
	Silver Sa'fa mandatory for all new buildings in Dubai; Golden/​Platinum optional; confirm jurisdiction applicability
	2026-11-04

	R19
	—
	Building No Objection Certificate - Electricity /​ Water
	DEWA
	Live official service; undated
	https:/​/​www.dewa.gov.ae/​en/​about-us/​service-guide/​builder-services/​building-no-objection-certificate
	Building NOC, asset protection and final connection are distinct
	2026-10-16

	R20
	—
	Utilities/​facilities within right of way NOC, service 318
	RTA
	Live official service; undated
	https:/​/​rta.ae/​wps/​portal/​rta/​ae/​home/​rta-services/​service-details?serviceId=318
	Confirm separate traffic, ROW and rail routes
	2026-10-16

	R21
	—
	Final Building Permit
	Dubai Development Authority
	Live official service; undated
	https:/​/​dda.gov.ae/​en/​planning-development/​construction/​permits-nocs/​final-building-permit
	DDA jurisdiction; final design approval prerequisite; demarcation before site activity
	2026-10-16

	R22
	—
	Trakhees Civil Engineering service-document register
	PCFC /​ Trakhees
	Live register; individual revisions vary
	https:/​/​pcfc.ae/​en/​Pages/​ServiceDocuments.aspx?D=Civil+Engineering+Department&E=Trakhees&S=Accreditation&T=Circulars
	Confirm active CED/​EHS permit, construction and completion documents
	2026-10-16

	R23
	ED-ISO19650-1; ED-ISO19650-2
	ISO 19650-1 concepts; ISO 19650-2 delivery
	ISO
	2018 editions
	https:/​/​www.iso.org/​standard/​68080.html
	Information/​appointment basis; companion part 1 source S01 in RESEARCH.md
	2026-10-16

	R24
	ED-ISO7817-1
	ISO 7817-1 Level of information need - Concepts and principles
	ISO
	2024, edition 1
	https:/​/​www.iso.org/​standard/​82914.html
	Purpose, actors, timing, objects; geometry, data and documents
	2026-10-16

	R25
	ED-RIBA-POW
	RIBA Plan of Work
	RIBA
	2020
	https:/​/​www.riba.org/​media/​sszn5kkt/​2020ribaplanofworktemplatepdf.pdf
	Stages 0-7; stage 3 Spatial Coordination; not statutory permission
	2026-10-16

	R26
	ED-ISO19650-5
	ISO 19650-5 Security-minded information management
	ISO
	2020; confirmed 2025
	https:/​/​committee.iso.org/​cms/​live/​live/​en/​sites/​isoorg/​contents/​data/​standard/​07/​42/​74206.html
	Information sensitivity/​access; not a CCTV technical approval specification
	2026-10-16

	R27
	ED-ISO19650-6
	ISO 19650-6 Health and safety information
	ISO
	2025, edition 1
	https:/​/​www.iso.org/​standard/​82705.html
	Delivery/​operational safety information; office requirements in BBM-STD-88
	2026-11-04

	R28
	ED-ISO19650-4
	ISO 19650-4 Information exchange
	ISO
	2022
	https:/​/​www.iso.org/​standard/​78246.html
	Exchange quality/​evidence; no universal office scoring threshold prescribed
	2026-10-16

	R29
	—
	Energy efficiency: emirate programmes
	UAE Government
	Live guidance; undated
	https:/​/​u.ae/​en/​information-and-services/​environment-and-energy/​water-and-energy/​energy-efficiency
	Other-emirate scheme screening; obtain local code editions/​services
	2026-10-16

	R30
	—
	Civil Protection Sector
	Abu Dhabi Civil Defence Authority
	Live official portal; undated
	https:/​/​www.adcda.gov.ae/​about-us/​Department2
	ADCD/​ADCDA route to confirm; DCD is Dubai authority
	2026-10-16

	R31
	—
	Objects outside obstacle limitation surfaces
	GCAA
	Safety Decision 2021-12, Issue 01
	https:/​/​www.gcaa.gov.ae/​en/​epublication/​EPublications/​Safety%20Decisions/​2021/​SAFETY%20DECISION%202021-12%20-%20OBJECTS%20OUTSIDE%20THE%20LIMITS%20OF%20OBSTACLE%20LIMITATION%20SURFACES%20-%20ISSUE%2001.pdf
	Aviation obstacle screening; current local airport/​crane route to verify
	2026-10-16

	R32
	—
	Work start notice for building permits
	TAMM /​ DMT
	Live official service; undated
	https:/​/​www.tamm.abudhabi/​ar-AE/​life-events/​business/​housing-construction/​consultants-contractors/​WorkStartNoticeforBuildingPermit
	Notice stage; not substitute for relevant permit/​prerequisites
	2026-10-16

	R33
	ED-DXB-LAW-3-2026
	Law No. 3 of 2026 Concerning the Quality and Safety of Buildings
	Government of Dubai
	Issued 27 February 2026; Official Gazette issue 764, 12 March 2026; in force from 11 May 2026 (O-DEC-156); applied by R42
	https:/​/​dlp.dubai.gov.ae/​Legislation%20Reference/​2026/​Law%20No.%20%283%29%20of%202026%20Concerning%20the%20Quality%20and%20Safety%20of%20Buildings.html
	Emirate law on existing buildings: Quality & Safety Certificate required after 20 years from completion, valid 10 years (5 years at 40+ years); asset-life obligation, not a design-permit rule
	2026-11-05

	R34
	ED-DM-9-1-2; ED-DM-9-1-3
	Circulars 9-1-2 and 9-1-3 on BIM model submission with building permits
	Dubai Municipality, Building Regulation and Permits Agency
	9-1-2: 13 October 2023, from 1 January 2024; 9-1-3: 15 January 2026, effective 1 April 2026
	https:/​/​dmpmedia.dm.gov.ae/​uploads/​2023/​10/​تعميم-BIM-9-1-2.pdf ; https:/​/​www.dm.gov.ae/​wp-content/​uploads/​2026/​02/​Circular-9-1-3.pdf
	Neither circular states an IFC version: use the IFC schema and export setup in the current Dubai BIM Standard (buildindubai.gov.ae/​bim), checked at project start; detail in BBM-STD-85
	2026-11-04

	R35
	ED-ADM-BIM
	ADM BIM Code of Practice; BIM Documentation Guidelines for Infrastructure; Infrastructure BIM Object Catalogue
	DMT /​ Abu Dhabi City Municipality
	Code of Practice October 2020 (cover v1, headers v1.1); Guidelines v1.0 October 2020; Object Catalogue v2.0 May 2021
	https:/​/​www.dmt.gov.ae/​adm/​-/​media/​Project/​DMT/​ADM/​E-Library/​0001-Jan-2022-Doc/​ADM-BIM-005Code-of-Practice.pdf
	Applies where the appointment or authority requires it; no universal Abu Dhabi building-permit BIM threshold
	2026-11-04

	R36
	ED-ISO16739-1
	ISO 16739-1 Industry Foundation Classes (IFC 4.3.2.0)
	ISO
	2024, edition 2
	https:/​/​www.iso.org/​standard/​84123.html
	Office default remains IFC 4.0.2.1 Reference View; IFC 4.3.2.0 by recorded approval only (O-DEC-105)
	2026-11-04

	R37
	ED-IDS
	Information Delivery Specification (IDS) 1.0
	buildingSMART International
	v1.0 final, June 2024
	https:/​/​github.com/​buildingSMART/​IDS/​releases
	Alphanumeric checks per exchange; name checker and version; schema conformance via the IFC Validation Service
	2026-11-04

	R38
	ED-BCF
	BIM Collaboration Format (BCF) 3.0
	buildingSMART International
	Final 18 June 2021; BCF 2.1 (2017) fallback
	https:/​/​github.com/​buildingSMART/​BCF-XML/​releases/​tag/​v3.0
	Issue exchange between coordination tools
	2026-11-04

	R39
	ED-ISO19650-3
	ISO 19650-3 Operational phase of assets
	ISO
	2020, edition 1
	https:/​/​www.iso.org/​standard/​75109.html
	Asset information handover and AIM update
	2026-11-04

	R40
	ED-COBIE
	COBie
	NIBS (NBIMS-US)
	Version as specified in the client EIR; default COBie 2.4 (NBIMS-US V3) unless the EIR names COBie v3 (NBIMS-US V4) (O-DEC-114)
	https:/​/​nibs.org/​nbims/​v4/​resources/​
	Delivered only when the EIR requires it
	2026-11-04

	R41
	—
	Dubai accessibility requirement named by the competent authority (DM /​ DDA /​ Trakhees)
	Competent Dubai authority
	Edition checked at project start and recorded in BBM-STD-51 §3
	https:/​/​www.dm.gov.ae/​municipality-business/​buildings-regulation-permits-agency/​
	Use with the DBC accessibility provisions [R17]; R04 is Abu Dhabi only
	2026-11-04

	R42
	ED-DM-11-9-1
	Circular (11-9-1) of 2026 applying Law No. 3 of 2026; guidance manual "Building Quality and Safety Certificate" (11-9-1-1)
	Dubai Municipality, Building Regulation and Permits Agency
	Circular 1 October 2026; manual May 2026
	https:/​/​dmpmedia.dm.gov.ae/​uploads/​2026/​10/​11-9-1.pdf ; https:/​/​dmpmedia.dm.gov.ae/​uploads/​2026/​10/​11-9-1-1.pdf
	Existing Dubai buildings 20 or more years from completion: certificate procedure and technical checklist; not a design-permit rule (AP-070)
	2026-11-05
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APPROVALS: STAGES, AUTHORITIES AND GATES

BA-STD-12 | Indicative UAE route. Confirm jurisdiction, applicability and exact activity permission.

PROJECT STAGE

Basis and jurisdiction
RIBA 0-1

Concept / planning
RIBA 2-3

Technical / permit
RIBA 3-4, by package

Construction
RIBA 5, by package

Completion / handover
RIBA 6

Use / renewal
RIBA 7

A submission receipt is not approval. A complete record is not permission. Verify conditions, scope, validity and the current revision.

AUTHORITY / EVIDENCE ROUTE

Client brief / OPR and verified plot, survey and use.
DMT municipality/planning or DM / DDA / Trakhees.
Freeze adopted codes, roles and approval screening.

Planning / developer; traffic and utility capacity.
Estidama or relevant Dubai green-building route.

Environment, heritage, aviation and asset NOCs if triggered.

Civil Defence; power / water; sewer; telecom; traffic.
Sector, security, gas and other conditional approvals.
Competent municipality / zone authority issues permit.

Early works / traffic / utility / crane permissions.

Approved products, shop design and mandatory inspections.

Design changes return to affected approval routes.

Final fire, utility, sustainability and sector clearances.
Witnessed tests, as-builts and completion certificate.
Confirm separate occupancy / partial-use authorisation.

Owner / FM tracks actual certificate expiry and conditions.
Competent municipality / sector regulator renewals.
Measure performance; retain residual-action ownership.

RELEASE GATE
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